## Sheet1
Keyword | Chunk
UL | ADNOC GAS HABSHAN GAS COMPRESSOR PLANT (HGCP) PKG 2 ADDENDUM TO DGS 1310 012 REV 1 DESIGN GENERAL SPECIFICATION BALL VALVES DOCUMENT No.: ADD-50092-HC-838-13-47-002 Rev.: A Page: 16 of 17 DISCIPLINE: 13 DOCUMENT TYPE: ADDENDUM CLASS: 1 6.5. Amendments to Section 5.0 – SPECIFICATION DEVIATION / CONCESSION CONTROL Replace MANUFACTURER With VENDOR 6.6. Amendments to Section 8.0 – DESIGN AND MANUFACTURE Amendments to Section 8.1 – GENERAL Replace The trunnion shall be integral with the ball. With The trunnion design shall be as per manufacturer’s standard. Replace VENDOR shall comply with additional requirements of SHELL MESC SPEs as listed below. Any contradictions between SPE’s and requirements in this specification shall be highlighted to COMPANY for resolution. 77/110 Ball valve Amendments to ISO 17292 77/303 Valves in Special Service 77/313 Valves with Corrosion Resistant Cladding / Overlay 77/130 Ball Valves (Amendments /Supplements to API 6D) 77/200 Testing of Valves –Fire Type Testing Requirements 77/302 Valves – General Requirements 77/310 Painting and Coating of Valves 77/312 Fugitive Emission Production Testing (Amendments / Supplements to ISO 15848-2) Any contradictions between above SPE’s and requirements in this specification shall be highlighted to COMPANY for resolution With Deleted. Add below point under section 8.1, • All Valves to be used in Fire Water Service shall be UL/FM listed as specified in Valve datasheet.