## Sheet1
Keyword | Chunk
NACE | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 8 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 Acronym / Reference Description MSAS Master Surface Annulus Safety Valve MTO Material take Off MTR Module Technical Room MV Master Valve **NACE** National Association of Corrosion Engineers NEMA National Electrical Manufacturers Association NFPA National Fire Protection Association NI North Island NIS Non Intrinsically Safe NPT National (American) Standard Pipe Taper (Thread) P&ID Piping and Instrumentation Diagram PAR Pre-Assembled Rack PAM Pre-Assembled Module PAU Pre-Assembled Unit PBU Production Build up PIMS Plant Information Management System PRM Plant Resource Manager PST Partial Stroke Test PSU Power Supply Unit PVL Package Vendor List PWT Produced Water Treatment RFI Radio frequency Interference RMMS Rotating Machine Monitoring System RP Recommended Practice RTU Remote Terminal Unit SCADA Supervisory Control And Data Acquisition
SIL | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 9 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 Acronym / Reference Description SCMS Substation Control and Monitoring system SIF Safety Instrumented Function **SIL** Safety Integrity Level SI South Island SIS Safety Instrumented System SMART Single Modular Auto ranging Transducer SOW Scope of Work SPDT Single Pole Double Throw SPI Smart Plant Instrumentation SRP Sulphate Reduction Plant TDM Transient Disturbance Monitoring TCP/IP Transmission Control Protocol / Internet Protocol TUV Technischer Überwachungsverein UAI Umm Al Anbar Island (West Island) UCP Unit Control Panel UL Underwriters Laboratories UPS Uninterrupted Power Supply UZ Upper Zakum WI West Island WP Work Package WV Wing Valve ZADCO Zakum Development Company Note 1. ADNOC Offshore was formed through the consolidation of two of ADNOC’s upstream oil and gas companies: Abu Dhabi Marine Operating Company (ADMA-OPCO) and Zakum Development Company (ZADCO).
PMI | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 13 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 CODE TITLE API 14Z Recommended Practice for Design and Installation of Electrical Systems for Fixed and Floating Offshore Petroleum Facilities for Unclassified and Class I, Zone 0, Zone 1 and Zone 2 Locations. API MPMS 20.3 Manual of Petroleum Measurement Standards Chapter 20.3 Measurement of Multiphase Flow. API 520 Part - I Sizing, Selection and Installation of Pressure Relieving devices in Refineries – Sizing and Selection API 520 Part-II Sizing, Selection and Installation of Pressure Relieving devices in Refineries – Installation API STD 521 Guide to Pressure Relieving and Depressurization Systems API STD 526 Flanged Steel Pressure Relief Valves API STD 527 Seat tightness for Pressure Relief Valves API RP-551 Process Measurement API RP-552 Transmission Systems API RP 553 Refinery Control Valves API RP-554 Process Instrument and Control API RP-555 Process Analysers API RP 557 Guide to Advanced control system API RP 576 Inspection of Pressure Relieving Devices API 578 Positive Material Identification (**PMI**) API 598 Valve Inspection and Testing API STD 607 Fire Test for Soft Seated Quarter Turn Valves API 609 Butterfly Valves Double Flanged, Lug and Wafer Type API-610 Centrifugal Pumps for Petroleum, Petrochemical and Natural Gas Industries Eleventh Edition API-STD 612 Petroleum, Petrochemical and Natural Gas Industries - Steam Turbines - Special-Purpose Applications Eighth Edition API STD613 API Standard 613, Special Purpose Gear Units for Petroleum, Chemical and Gas Industry Services-Sixth Edition API STD617 Axial and Centrifugal Compressors and Expander-compressors for Petroleum, Chemical and Gas Industry Services Ninth Edition API STD 618 Reciprocating Compressors for Petroleum, Chemical, and Gas Industry Services Fifth Edition API STD619 Rotary-Type Positive-Displacement Compressors for Petroleum, Petrochemical and Natural Gas Industries Fifth Edition API 670 Machinery Protection Systems
NACE | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 17 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 4.2.5. National Association of Corrosion Engineers (**NACE**) CODE TITLE **NACE** MR-0175 / - ISO 15156 Petroleum and Natural Gas industries- Materials for use in H2S containing environments in Oil and Gas Production. 4.2.6. International Electrotechnical Commission (IEC) CODE TITLE - IEC 60028 International Standard of Resistance for Copper - IEC 60034 Rotating Electrical Machines - IEC 62443 Industrial Communication Network - IEC 60068 Basic Environmental Testing Procedures for Electronic Components and Electronic Equipment - IEC 60079 Electrical apparatus for Explosive gas atmospheres - IEC 60092- 360 Electrical installations in Ships: Insulating Materials for Shipboard and Offshore Units, Power, Control, Instrumentation, Telecommunication Cables - IEC 60092- 370 Electrical installations in Ships: Guidance on Selection of cables for telecommunication & data transfer including Radio frequency cables - IEC 60092-376 Electrical installations in ships :Cables for control and instrumentation circuits 150/250V (300V) - IEC 60099-5 Surge Arrestors: Selection and Application Recommendations - IEC 60189-1 to 3 Low-frequency Cables and Wires with, PVC insulation and PVC Sheath - IEC 60227-1 Polyvinyl Chloride Insulated Cables of Rated Voltages up to and including 450/750 V: General Requirements - IEC 60228 Conductors of Insulated Cables - IEC 60245 Rubber Insulated Cables – Rated voltages up to and including 450/750 V - IEC 60331 Test for Electric Cables Under Fire Conditions (Fire resistant) - IEC 60332 Test for Electric Cables and Optical Cables Under Fire Conditions (Flame retardant) - IEC 60529 Degrees of Protection provided by Enclosures(IP Code) - IEC 60534 Industrial Process Control Valves - IEC 60584 Thermocouples - IEC 60751 Industrial Platinum Resistance Thermometer Sensors - IEC 60754-1 Part 1: Halogen Release Under Fire Conditions - IEC 60754-1-2 Test on Gases Evolved During Combustion of Materials from Cables - Part 1: Determination of the Amount of Halogen Acid Gas
NACE | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 27 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 7.2 INGRESS PROTECTION All field instruments and Junction Boxes shall have a certified Ingress Protection of IP-66 in accordance with IEC-60529, as a minimum. All Outdoor Cabinets and Panels shall have a certified Ingress Protection of IP 65 as a minimum. All Indoor Cabinets and Panels shall have a certified Ingress protection of IP 54 as a minimum. All field instruments, cabinets and panels exposed to direct sun light shall be provided with sun shades or canopies as applicable. 8.0 SPECIALSOUR SERVICE REQUIREMENTS 8.08.1 SOUR SERVICE REQUIREMENTS All the field instruments including accessories in hydrocarbon services shall conform to the requirements of **NACE** Standards MR-0175/ISO15156 (latest edition). The use of double block and bleed / single block valves for instrument isolation shall be in line with Isolation Philosophy document (Doc. No. E1150-GD-2000-F-0006). All Oil & Gas as well as hazardous chemical instrument bleed, blow down and drains shall be routed to closed drain or flare with appropriate piping / tubing in accordance with P & I diagrams and job specifications for “Vent And Drain Philosophy”, (Doc. No.E1150-GD-2000-F-0007). 8.2 LETHAL SERVICE REQUIREMENTS For lethal service and pipe class rating of 1500# and above, hard pipe (instead of impulse tubing) shall be used for hook-up of transmitters. All Oil & Gas as well as hazardous chemical instrument bleed, blow down and drains shall be routed to closed drain or flare with appropriate piping / tubing in accordance with P & I diagram and job specifications for “Vent And Drain Philosophy”, (Doc. No.E1150-GD-2000-F-0007). 9.0 SOFTWARE TO BE USED Instrument Sizing Intergraph SPI (INToolsINTOOLS) Version 13.1 Instrument Database Intergraph SPI (INToolsINTOOLS) Version 13. Instrument Drawings Intergraph SPI (INToolsINTOOLS) Version 13.and AutoCAD latest Version Other Documents Intergraph SPI (INToolsINTOOLS) Version 13., MS Word and Excel Modelling Intergraph SP3D The detail engineering design shall utilize Intergraph's SmartPlant Instrumentation (SPI or previously termed as `INtools Intools”) to develop the instrumentation database and generate the applicable PROJECT deliverables in compliance with “SPI implementation Procedure” (E1150-PB-2000-G-0025). The application software versions for SPI, oracle, operating system and other design software's will be in compliance with the requirements specified in the Project document “SPI Implementation Procedure (E1150-PB-2000-G-0025).
NACE | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 30 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 INSTRUMENT TYPE PROCESS / VESSEL CONNECTION INSTRUMENT CONNECTION Pressure transmitter and DP transmitter (on vessel, Sour services) 2” flanged x ½” OD ½” NPT(F) x ½” OD Inst. with diaphragm seal (pipe or vessel) 3” flanged 3” flanged Temperature Instruments Thermowell on pipe 1 1/2” flanged or 2” flanged (Note 12) 1 1/2” flanged or 2” flanged (Note 12) Thermowell on vessel 2” flanged 2” flanged Refer project Instrument Process hook-up Drawing-AGI/CI (E1150-A3-2000-J-2009), Instrument Process hook-up Drawing-ETI/NI (E1150-A3-2100-J-2009), Instrument Process hook-up Drawing-UAI/WI (E1150- A3-2300-J-2009), Instrument Process hook- up Drawing-ASI/SI (E1150-A3-2200-J-2009). Notes: 1. For diaphragm seal, the seal is the instrument connection. 2. Instrument drain/vent shall be connected as per Instrument hook-up drawings and Piping and Instrumentation Diagram (P&ID). 3. Flanged end connection rating shall be 300# RF, as a minimum for Instruments mounted on Process equipment. 4. For pipe class with higher ratings, instrument connection size shall be as per piping material specifications as applicable. 5. The stand pipe connections to the equipment will be 3”. 6. The type of flange shall be in accordance to piping material specifications (PMS). 7. Threaded connections shall be avoided in sour service. 8. For GRP pipes Instrument side flange shall be metallic. 9. Flange material shall be governed by the process service. 10. Threaded/ Welded connections shall be avoided in Lethal service 11. Instrument Impulse tubing shall be 12 mm O.D, , 0.89 mm minimum wall thickness, SS-316L. However, selection of materials shall be chosen based on process condition. Material for sour service shall comply with applicable COMPANY & **NACE** standards MR0175/ - ISO 15156. For lethal service and pipe class rating of 1500# and above, hard pipe (instead of impulse tubing) shall be used for hook-up of transmitters. 12. The Thermowell connection Size for line shall be 1 ½” NB OE 2” NB depending on the piping material specification for the line. Refer Piping design and construction standard (E1150-BD-2000- P-0002) and Piping Material specification (E1150-TS-2000-P-0001) for details. 13. Diaphragm seals are required for level instruments in lethal, severely dirty, corrosive, hazardous fluids, or fouling service. Pressure instruments for measurement in non-clean applications including slurry, dirty, highly viscous fluid will use diaphragm seal type transmitters with flushing ring. 11.0 ELECTRICAL-INSTRUMENTATION INTERFACE Substation Automation Systems with Intelligent MCCs using IPCMS will be implemented for the Island Process facilities by electrical discipline. The Start/Stop commands from the BPCS to the IPCMS and the Motor status signals to the BPCS from the IPCMS shall be communicated using redundant MODBUS TCP/IP protocol.
SIL | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 31 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 Status signals from the Substation Control & Monitoring System (SCMS) and the Load Management, Load Shedding (LMLS) system and the Transient Disturbance Monitoring (TDM) system to the BPCS shall be communicated using redundant MODBUS TCP/IP protocol. All electrical interfaces to the SIS system shall be hardwired. The ESD signals from the SIS shall use volt free contacts powered by the receiving system. Interposing Relays shall be used (as necessary) to segregate MCC voltages (greater than 24 V DC/AC) from the BPCS. and SIS I/O equipment which shall use 24 V DC. All interface signals from SIS to MCC shall be through interposing relays. Any relays used for Safety Instrumented Functions (SIFs) shall be certified with the applicable **SIL** rating. New interposing relay panels shall be provided, or existing interposing relay panels shall be modified by MAC as per ICSS adequacy study report. Refer MAC Scope of work (E1150-SW-2000-J-0001) and Specifications for ICSS (E1150-TS-2000-J-0034) for details. The communication links shall be monitored and failure shall be alarmed in BPCS using watch dog logic. New EAMS shall be provided for existing and new facilities in AGI,ETI, UAI and ASI. The existing Plant Resource manager (PRM) will be integrated with new EAMS to fetch asset health status and display in PRM Client. Refer MAC Scope of work (E1150-SW-2000-J-0001) for further details on EAMS integration with existing ICSS and PRM. 12.0 HVAC-INSTRUMENTATION INTERFACE The HVAC control system for all the buildings shall be interlocked with the smoke / fire and gas detection system to shut down the HVAC system upon receipt of a signal from the smoke/ fire and gas detection system. Flammable HC gas and toxic gas (H2S) detectors will be provided at the Air Lock and HVAC air inlets of all the buildings irrespective of manned or unmanned. Motorised fire & Gas Dampers shall be provided at fresh air intakes, outlets and rooms which are protected by clean agent maintaining concentrations. These dampers shall be closed and building HVAC will be shut down upon confirmed Fire or confirmed gas detection. HVAC Control Panel shall be PLC based, with redundant controller for automatic operation. HVAC Control panels operation status shall be linked to BPCS, as required and shall have hardwired interface with the Fire & Gas System panels and motor control centres. Motorised fire & Gas dampers shall be shut down from HVAC control panel. Existing philosophy shall be followed in all aspects related to interface and integration with ICSS. Critical signals interchanged between the HVAC systems and the SIS and F&G systems shall be hardwired using volt free contacts in the outputs of both systems. The rest of signals interchanged with BPCS for normal operation & monitoring shall be communicated using redundant MODBUS TCP/IP communication. Any relays used for Safety Instrumented Functions (SIFs) shall be certified with the applicable **SIL** rating.
SIL | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 35 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 Hydraulic fluid shall be SHELL IRUS Fluid C for all hydraulic actuated On-Off and ESD valves on Islands other than well head actuated valves. Whereas Castrol Hyping AWH15 or ADNOC Lube ISO 46 shall be used for valves operated by HSSS of well pad area. The use of Synthetic oil is not acceptable. 15.3 PNEUMATIC SUPPLIES The Instrument air supplies shall be as follows: Design Pressure 175 psig Maximum Pressure 130 psig Normal pressure 109 psig Minimum pressure 58 psig Dew Point Minus 40 °C The valve actuators and the pneumatically powered valve accessories shall be sized using the above minimum pressure but also shall be suitable for the above design pressure. Control Valve Actuators should be designed to operate on a range of 3 to 15 psig. 16.0 SELECTION OF INSTRUMENTATION 16.1 GENERAL Instruments and Systems shall comply with the following design criteria, as a minimum: All instruments, control system including valves, actuators and accessories shall be purchased from reputed manufacturers on the COMPANY approved VENDOR list with proven track record of installation in similar Oil & Gas facilities and shall be standardized with the same manufacturer throughout the Islands as far as practical. Latest instrument models shall be provided. Obsolescence of models of ICSS components that are part of project scope of work, Detectors and Sensors shall be critically verified during technical review and evaluation. Project material shall have at least 30 years of support available from the start of operation. Adequacy of the existing systems hardware, software, licenses, and its compatibility with any new added hardware, software, licenses part of 1 MMBPD project shall be verified as part of adequacy checks of the existing systems through existing system OEM. BPCS Instruments shall not be used for SIS duties and vice versa. In case a particular process variable needs to be used both for control and protection functions, two separate transmitters shall be provided. This is also applicable for Packages Units. All instruments (including valves and actuators) used in Safety applications (SIFs) shall be **SIL** certified by TUV or equivalent. All necessary data required for **SIL** verification shall be obtained from the relevant VENDORS. The BPCS shall be Foundation Fieldbus compatible. The SIS and FGS systems shall be HART compatible. For Packages monitored and controlled by the BPCS, the package Instruments shall be FF compatible.
SIL | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 37 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 • Process unit and critical Utility unit Inlet and Outlet shutdown valves, the tripping of which may lead to a complete facility shutdown or to shutdown of a key process unit. • Blow down applications and any Actuated On-Off valve on a SIF duty. • PST and SOV test option shall be applied for all valves including BDVs with size 3" and above, regardless the assigned **SIL** rating for that valve. • Valves including BDVs with sizes less than 3" shall not be provided with PST and SOV test. All Field Switch devices (e.g. Pressure Switches), wherever used, shall have two Single Pole Double Throw (SPDT) contacts (2A, 24V DC). Field instruments and/or devices shall have dedicated tappings and process isolation valves. The first Isolation Valve on each tapping point shall be provided by Piping as per the Project Piping Material Specification. Pressure transmitters and pressure gauges shall have a 2-valve Instrument manifold for instrument isolation. All pressure indicators associated with X-mas trees shall be provided with overrange protectors. Differential pressure transmitters (Flow, Level and DP) shall have a 5-valve Instrument manifold for instrument isolation. Instrument manifolds shall be integral and connected directly to the transmitter. For hard pipe hookup, the manifolds shall be provided with flange adapter/kidney flange with the nipple welded for process and vent connection. Pressure instruments for measurement in non-clean applications including slurry, dirty, highly viscous fluid will use diaphragm seal type transmitters with flushing ring. Instrument air take off points shall be provided with isolation valves and spare ones shall be plugged. Instrument air shall be supplied through SS316L piping as per pipe class A51E of piping material specifications. Instrument Process Wetted part materials shall be suitable for the process fluid operating and design conditions. Valve body and trim materials shall be suitable for the process fluid operating and design conditions. Trim Material shall be SS316L (as a minimum) or as required for the application (as per the associated Project Specifications). All the electronic instruments shall have two ISO M20 cable entries to accommodate certified (Ex “d”) cable glands. Adapters shall not be used to convert NPT cable entries to Metric Parallel cable entries. Spare cable entries shall be plugged with certified SS316L plugs. Instruments with flying leads are not acceptable and all leads shall be terminated on terminal blocks in an integral junction box with terminals to connect the incoming field cables.
SIL | PROJECT No. E1150 ENGINEERING,PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 SURFACE FACILITIES PROJECT INSTRUMENT & CONTROL DESIGN BASIS Company Doc No: E1150-BD- 2000-J-0001 Rev.: A2 Page 42 of 56 Contractor/Eng Document No: 217601C- 000-JSD-1500-0001 16.7 CONTROL VALVES Globe body valve shall be the first choice for valves up to 12” size. Cage guided valves shall only be used in clean service. They shall be avoided for highly viscous fluids or services and where solids are likely to be present or coking may occur. As a minimum all Control Valves shall be offered with valve seat leakage to Class IV as per - IEC 60534-4. TSO shall mean Class VI leakage (bubble-tight shutoff) and shall be provided only when specified in the Data Sheet. Control Valves used in the minimum recirculation line at the discharge of the pumps and flare Control Valves shall have leakage rate of Class V. The detailed requirements for Control Valves are stated in the Project Specifications for Control Valves (Doc. No. E1150-TS-2000-J-0006) , Piping Specification for Gate, Globe, Check and Needle Valves (E1150-TS-2000-P-0016) and the associated Project Instrument Data Sheets. 16.8 ACTUATED ON-OFF VALVES Actuated On-Off valves shall be designed to be Fail- Safe (unless otherwise stated on the associated P&IDs and Instrument Valve Data Sheets) and the Actuator shall be the Fail-Safe spring return type (unless otherwise specified on the associated Instrument Valve Data Sheets). Actuated On-Off valves used for safety applications shall be suitable for the Safety Integrity Level (**SIL**) specified on the associated Instrument Valve Data Sheet. The actuator shall be selected based on stroking time specified in the associated Instrument Valve Data Sheet. Valve VENDOR shall be responsible for the mechanical compatibility between the valve and actuator. Actuator shall be supplied with all the necessary accessories such as solenoid valves, quick exhaust vent valve etc., as per the requirements of this specification and associated Instrument Valve Data Sheets. The detailed requirements for Actuated on-off Valves are stated in the Project Specifications for Actuated On-Off Valves (Doc. No. E1150-TS-2000-J-0002) , Piping Specification for Ball Valves and IDBB Valves (E1150-TS-2000-P-0015) and the associated Project Instrument Data Sheets. 16.9 SAFETY RELIEF VALVES Sizing, Selection and installation of safety relief valves shall be as per API Std 520. The orifice designations, materials, area, end connection sizes and rating shall be as per API Std. 526 for Flanged Steel valves. Seat tightness requirements and testing shall be as per API Std. 527. API Std 521 shall be used as a general guideline for examining the causes of overpressure and determining individual relieving rates.
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 9 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 FISCO Fieldbus Intrinsically Safe Concept FM Factory Mutual FMR Field Manual Reset FO Fail Open GRP Glass Reinforced Plastic H2S Hydrogen Sulphide HART Highway Addressable Remote Transducer HEMS Helicopter Emergency Medical Services HSE Health, Safety and Environment IEC International Electro-technical Commission IP Ingress Protection IS Intrinsic Safety ISA International Society of Automation ISO International Organization for Standardization LER Local Equipment Room MAC Main Automation Contractor MAST Maximum Allowable Stem Torque MAWP Maximum Allowable Working Pressure MMBD Million Barrels per Day N2 Nitrogen **NACE** National Association of Corrosion Engineers NDT Non-Destructive Testing NEMA National Electrical Manufacturers Association NPT National (American) Standard Pipe Taper (Thread) NPT National (American) Standard Pipe Taper (Thread) OEM Original Equipment Manufacturer P&ID Piping and Instrumentation Diagram
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 10 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 PAM Pre-Assembled Module PFD Probability of Failure on Demand PMS Piping Material Specification PST Partial Stroke Test PSV Pressure Safety Valve PWT Produced Water Treatment QA/QC Quality Assurance/ Quality Control QAR Quality Assessment Report RFI Radio Frequency Interference RP Recommended Practice RTJ Ring Type Joint SDV Shutdown Valve SIF Safety Instrumented Function **SIL** Safety Integrity Level SOV Solenoid Valve SPDT Single Pole, Double Throw SS Stainless Steel TSO Tight Shut-Off (valve) UAE United Arab Emirates UAI Umm Al Anbar island UZ Upper Zakum WP Work Pack WPQR Welder Performance Qualification Record WPS Welding Procedure Specification WQT Welder Qualification Test
ISO 5208 | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 12 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 4.2 REFERENCE CODE AND STANDARDS 4.2.1 International Standards Organization (ISO) CODE TITLE - ISO 9001 Quality Management System – Requirements - ISO 1219 Fluid Power Systems and Components – Graphic Symbols and Circuit Diagram - ISO 17292 Metal Ball valves for petroleum, petrochemical and allied industries - ISO 10497 Testing of Valves: Fire type testing requirements - ISO 15848 - 1 Industrial Valves – Measurement, Test and Qualification Procedures for Fugitive Emissions (Classification Systems and Qualifications Procedures for Type Testing of Valves & Parts) - ISO 15848 – 2 Industrial Valves – Measurement, Test and Qualification Procedures for Fugitive Emissions (Production Acceptance Test of Valves) ** - ISO 5208** Industrial Valves: Pressure Testing of Metallic Valves - ISO 5211 Industrial valves - Part-turn actuator attachments - ISO 19011 Guidelines for Auditing Management Systems - ISO 10474 Steel and steel products - Inspection documents - ISO 12490 Mechanical Integrity and Sizing of actuators and mounting kits for Pipeline valves - ISO 9004 Quality management -Quality of an organization - Guidance to achieve sustained success 4.2.2 Instrument Systems and Automation Society (ISA) CODE TITLE ISA TR96.05.01 Partial stroke testing of automated valves 4.2.3 American Petroleum Institute (API) CODE TITLE API 6D Specification for Pipeline Valves (Gate, Ball and Check) API 6FA Specification for Fire Test of Valves
PMI | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 13 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 CODE TITLE API 552 Transmission System API 578 Positive Material Identification (**PMI**) API 598 Valve Inspection and Testing API 607 Fire Test for Soft-Seated Quarter-Turn Valves API STD 608 Metal Ball Valves - Flanged, Threaded, and Butt-Welding Ends API 2218 Fire Proofing Practices in Petroleum and Petrochemical Plants API STD 609 Butterfly Valves: Double-flanged, Lug- and Wafer-type 4.2.4 American Society of Mechanical Engineers (ASME) CODE TITLE ASME B 1.20.1 Pipe Threads, General Purpose (Inch) ASME B 16.10 Face to Face and End-to-End Dimensions of Valves ASME B 16.47 Large Diameter Steel Flanges: NPS 26 Through NPS 60 Metric/Inch Standard ASME B 16.5 Pipe Flanges and Flanged Fittings NPS ½ Through NPS 24 Metric/Inch Standard ASME B16.20 Metallic Gaskets for Pipe Flanges ASME B16.34 Valves - Flanged, threaded and welding ends ASME B31.3 ASME Code for Process Piping ASME B 46.1 Surface Texture (Surface Roughness, Waviness and Lay) ASTM A182 Standard Specification for Forged or Rolled Alloy and Stainless Steel Pipe Flanges, Forged Fittings, and Valves and Parts for High-Temperature Service ASTM A269/269M Standard Speciﬁcation for Seamless and Welded Austenitic Stainless Steel Tubing for General Service ASTM A479 Standard Specification for Stainless Steel Bars and Shapes for Use in Boilers and Other Pressure Vessels ASTM B677 Standard specification for UNS 08925, UNS 08354 and UNS 08926 Seamless Pipe and tube
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 14 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 4.2.5 National Association of Corrosion Engineers (**NACE**) CODE TITLE **NACE** MR0175/ - ISO 15156 Petroleum and Natural Gas Industries – Materials for Use in H2S Containing Environments in Oil and Gas Production ANSI/**NACE** MR0103/ - ISO 17945 Metallic Materials resistant to Sulfide Stress Cracking in corrosive petroleum refining environments **NACE** TM0177 Laboratory Testing of metals for resistance to sulfide stress cracking and stress corrosion cracking in H2S environments 4.2.6 International Electrotechnical Commission (IEC) CODE TITLE - IEC 60079 (All Parts) Electrical apparatus for Explosive gas atmospheres - IEC 60085 Electrical insulation - Thermal evaluation and designation - IEC 60529 Degrees of Protection provided by Enclosures (IP Code) - IEC 60534-4 Industrial-process control valves. Inspection and routine testing - IEC 60534-5 Industrial-process control valves marking - IEC 60947-5-2 Low-voltage switchgear and control gear - Part 5-2: Control circuit devices and switching elements - Proximity switches - IEC 61000 (All Parts) Electromagnetic Compatibility (EMC) - IEC 61158 Digital Data Communications for measurement and Control – Field Bus for use in Industrial Control System - IEC 61508 Functional safety of Electrical /Electronic/ Programmable electronic safety related systems - IEC 61511 Functional safety – Safety Instrumented Systems for the Process Industry - IEC 61326-1 Electrical Equipment for Measurement, Control and Laboratory Use – EMC Requirements, Part-1: General Requirements
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 17 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 • Process stream Isolation valves. • Isolation valves applications requiring sequentially timed opening/ closing operations. This Project is an extension of the UZ750 Project. Existing philosophy shall be followed. Any deviation shall be highlighted clearly for COMPANY review. The Valve selection responsibility is assigned to the Valve VENDOR and necessary guidelines for selection are also included. The VENDOR shall be fully responsible for meeting both the General and Specific technical requirements of this specification inclusive of the referenced documents in respect of design, materials and services. 6. GENERAL REQUIREMENTS Actuated On-Off valves shall be designed to be Fail-Safe (unless otherwise stated on the associated P&IDs and Instrument Valve Data Sheets) and the Actuator shall be the Fail- Safe spring return type (unless otherwise specified on the associated Instrument Valve Data Sheets). Actuated On-Off valves used for safety applications shall be suitable for the Safety Integrity Level (**SIL**) specified on the associated Instrument Valve Data Sheet. The **SIL** report and PFD values shall be for the whole assembly as one unit, this including valve body, actuator, control components, SOV, Quick Exhaust Valve, etc and any other accessories Valve VENDOR is responsible to provide the **SIL** report for the complete assembly as above. The **SIL** report for the complete assembly shall be reviewed and certified by a recognized and COMPANY approved agency like TUV or Exida. This certification shall be submitted with the bid. All electronic, local station and Panels shall be protected by GRP sunshade. ESD valves shall be fire-rated to an approved standard, but additionally passively fire protected if thermal radiation is above the fire-rating of the valve or above 32 kW/m². 6.1 HAZARDOUS AREA REQUIREMENTS The detailed requirements for Hazardous Area are stated in the Project Document “Instrument & Control Design Basis” (E1150-BD-2000-J-0001). The minimum hazardous area protection certification, irrespective of area specified (safe or hazardous area), shall be Flame proof/ Explosion proof or FISCO certified suitable to Zone 1, Gas group IIB, Ignition temperature class T3 at ambient Temperature of 55 °C as per IEC-60079, unless otherwise specifically stated in Instrument Valve Data Sheet. Instruments installed in hazardous areas shall be certified by an Approved national authority (e.g. CSA, UL, BASEEFA, FM, CESI, LCIE, TUV) to the appropriate sections of IEC-60079. All such equipment shall carry apparatus marking as per IEC. Additional ATEX marking shall be applicable for equipment conforming to CENELEC / IEC as per EU Directive ATEX 2014/34/EU; whereas equipment conforming to North American Practices / NEMA shall carry AEx apparatus marking.
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 20 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 Predicted sound pressure level shall not exceed 85 dBA at 1 m downstream and 1 m distance from valve surface. The fluid velocities at the outlet of the valve body shall not exceed the maximum permitted value for the valve body. Valve body and Trim materials shall be suitable for all the operating conditions as specified in the associated Instrument Valve Data Sheet. All Valves in hydrocarbon service (Sour service) shall be certified for Fugitive Emission Certification as per - ISO 15848 Part 1 & Part 2. Wherever fugitive emission tests are specified in the Instrument Valve Data Sheets, valves shall be subjected to prototype and production tests in accordance to - ISO 15848 Part 1 and Part 2 respectively and compliance certificate shall be provided for all the applicable valves. Fugitive emission tightness class shall be according to Instrument Valve Data Sheet. Selection of valves, extension of qualification to untested valve, etc. shall be as per - ISO 15848 Part 1. The inspection & testing of the valve shall be as per the requirements of respective manual valve Piping Specifications (Ball or Butterfly) listed in section 4.3. All ESDV and BDV shall be provided with the following buttons on local panel in field: Open, Close, Reset and Spare. Necessary software license shall be provided for valvelink software. EPC Contractor shall arrange at site for the valve tuning / signature in valvelink software by vendors during commissioning. Partial Stroke Testing Actuated On-Off valves for the following services shall be equipped with partial stroke testing facilities. • Shutdown valves and Isolation valves on the main Plant/Facility Inlet and Outlet lines. • Process unit and critical Utility unit Inlet and Outlet shutdown valves, the tripping of which may lead to a complete facility shutdown or to shutdown of a key process unit. • Blow down applications and any Actuated On-Off valve on a SIF duty. • PST and SOV test option shall be applied for all valves including BDVs with size 3" and above, regardless the assigned **SIL** rating for that valve. • Valves including BDVs with sizes less than 3" shall not be provided with PST and SOV test. Partial Stroke Testing shall be implemented using the Position Control Methodology as per ANSI ISA TR96.05.01. The Partial Stroke Testing facility shall allow both Manual and Automatic Partial Stroke Testing. The offered Valve Positioner shall be certified as meeting the requirements of - IEC 61508 for incorporation into Safety Instrumented Function (SIF) loops that are rated to Safety Integrity Level 3 (SIL3). Positioner housing shall be SS316L and painted. Positioners for PST shall be smart devices that are capable of initiating a valve stroke from normal position to a predetermined value, returning the valve to its normal position and recording and time-stamping the resulting actuator pressure/valve position/time profiles for transmission to ICSS via HART communication. Valve position feedback to the positioner shall not rely on mechanical connection between the positioner and the valve stem (non-contact sensing).
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 21 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 Positioner interface to ICSS shall be 4 – 20mA +HART Enclosure cable entries shall be threaded M20 x 1.5 to accept cable glands. Positioner housing shall be 316L stainless steel and have minimum enclosure ratings of IP 67. The positioner shall be fitted with two pressure gauges, for supply inlet pressure and control outlet pressure. The positioner shall be certified as, • Suitable for use in safety applications up to **SIL** 3 • Designed to intrinsic safety Ex ib minimum in accordance with - IEC 60079-11 Positioner shall be Fisher DVC6200S or latest DVC model. The Partial Stroke Testing scheme shall be configured in the BPCS/SIS and AMS. All test data shall be recorded in the BPCS Historian (valve position data) and in AMS (PST test results). The Partial Stroke Testing Scheme shall also include testing of the solenoid valve. Solenoid valve will be tested generating a pulse in the solenoid activating signal by means of the ESD system. This pulse should be as short as possible to avoid or limit to a minimum movement of the isolation valve actuated by the solenoid. It’s important to notice that minimum possible pulse length is limited by the scan cycle of the ESD controller (at present 300 ms). The solenoid selection to be consulted with MAC and the same shall be simulated during the MAC FAT utilizing actual solenoids and PST set up. The recommended Partial Stroke Testing design scheme for Spring Return & Double Acting Pneumatically Operated Valves is shown in APPENDIX1. The On-Off Valve, Actuator, Positioner and all necessary accessories shall be supplied completely assembled, properly wired and tubed and fully tested with a copy of the Test Valve Signature on disk. Partial Stroke testing plug-in software shall be supplied by Valve VENDOR for installation in the AMS by MAC. Casting shall be free from injurious blowholes, porosity, shrinkage, faults, cracks or other defects. Reworked castings with defects plugged, welded, burned or impregnated are unacceptable. Valve Test Actuated On-Off valves for Emergency isolation, Blowdown applications shall meet the requirements of API 598, BS EN 12266, API 6FA. All the Actuated On-Off valves shall meet the requirements of API 598. Material Body and Trim Material selection shall be as per the requirements of the Piping Specifications and Valve Data Sheets identified in clause no. 4.3, Specification for Instrument Material Selection (Doc. No. E1150-TS-2000-J-0010) and the associated Instrument Data Sheets. Valve Materials of Construction shall be electro-chemically and galvanically compatible with the associated Piping and Flange Bolt/Gasket materials. Valves, Actuators, Positioners and all accessories shall be designed to have a minimum life expectancy of thirty years. Actuated On-Off valves shall be equipped with Local Control Panel facility for the valves designated as Emergency Shutdown Applications (SDV or ESDV), Emergency Blowdown
ISO 5208 | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 22 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 Applications (BDV or EDPV), Process stream Isolation (including DB & B) valves and Isolation valves applications requiring sequentially timed opening/ closing operations. All the accessories and control components (e.g. Logic components, Miniature Valve, SOV, Partial Stroke devices, Open/Close Push Buttons, Filter Regulator etc.) shall be housed in a painted SS 316L Local Control Box, which shall be suitable for highly corrosive, humid, salt laden marine environment, weatherproof to IP66 as a minimum. All Accessories, plates, box etc shall be in SS 316/L exposed to outside ambient condition shall be in SS 316L. 7.2 ACTUATED ON-OFF BALL VALVES Fire safe Quarter-turn Trunnion-mounted Ball valves with Dual Seat Seals shall be provided for ESD Isolation and Blow-Down valves. Double Block and Bleed (DB&B) Fire safe Quarter-Turn Trunnion-mounted Full Bore or Reduced Bore Ball valves shall be provided for Process Isolation valves where specified in the associated Instrument Valve Data Sheets. The Bleed outlet shall be provided with a pressure gauge and/or valve when specified on the Instrument Valve Data Sheet, otherwise, the bleed outlet shall be plugged. Fire safe valves shall meet the requirements of API 607/API 6FA/ - ISO 10497 and shall be API 607/API 6FA/ - ISO 10497 certified. Split body arrangement (for easy replacement of ball and seals) is the preferred design. The inner seal shall be a surface contact based metallic face seal with outer soft seal. Ball valves used as Isolation valves for process or metering applications shall be Double Block and Bleed type (DB&B). Quarter-Turn rotary action shall preferably be through rack and pinion linkage arrangement. Scotch yoke mechanism may be employed for spring-opposed actuators. Adjustable mechanical stops (independent of any actuator travel stops) shall be provided in the valve. ESD valves shall provide tight shut-off (TSO) where specified. Valves shall be subject to “Seat Tightness Tests” as prescribed in API 598 and comply with “Acceptable Seat Test” criteria defined in ** - ISO 5208**. In liquid service for tight shut-Off ESD valves ** - ISO 5208** Rate B shall be used and for non- TSO Rate CC (equivalent to API 598) shall be used. In gas service for TSO ESD valves ** - ISO 5208** Rate A shall be used and non-TSO API 598 shall be used. EBD valves shall meet the requirements of ** - ISO 5208** Rate A. Valve design, dimensions, marking and rating shall comply with API 6D. 7.3 TRIPLE OFFSET BUTTERFLY VALVES • Butterfly valves shall be designed as per API 609 and shall be used up to 600# pressure class only.
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 29 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 7.6 LIMIT SWITCHES Limit switches shall be Proximity type, as specified in Instrument Valve Data Sheet. Two limit switches (open and close) shall be provided. Accuracy / Repeatability: Within 3% of valve travel limits. Output contact rating shall be 1.0 A at 24V minimum. Contact form shall be SPDT, unless otherwise specified. Limit switches connected to the BPCS shall be of the FF type. All other limit switches shall have 2A, 24VDC SPDT contacts, as specified in the instrument valve datasheets. EOL resistor (by others) shall be provided for local push buttons in the JB side inline with the existing philosophy. Limit switches shall be as follows: • Directly activated by the valve stem or shaft position • Operate within 3% of valve travel from respective open and closed limits • Protected to prevent mechanical disturbance/malfunction • Failure mode leads to alarm condition • Adjustable so they operate at the correct point in the valve travel • Limit switches used on ESDV valves shall be minimum **SIL** 2 certified. Hermetically sealed Inductive Proximity switches shall be provided. Minimum sensitivity gap shall be 4 mm. The proximity switches for open and close shall be independent of each other in its field function. Switch with galvanically isolated Amplifier shall be fail-safe for lead or power supply failure. The Proximity switches shall be delivered housed in a termination box of SS316L with the enclosure suitably certified for Ingress Protection & Electrical Hazardous area. (Flying leads from proximity switches are not acceptable). Separate entries for open and close switch wiring on the termination box shall be provided, unless otherwise specified. Proximity switches shall be in accordance with DIN 19234: Measurement and Control Electrical distance sensors-DC interface for distance sensor and Signal converter. The combination of proximity switch and sensing circuit shall be fail-safe. 7.7 HAND WHEEL Hand wheel shall not be provided on ESD valves. Hand wheel on other applications shall be provided only when specified in Instrument Valve Data Sheet. Manual hand wheel for HV and manual operated isolation valves for XVs shall be provided for maintenance during failure. Note: Hand wheel or Manual Override actuation may be provided for process isolation valves through a de-clutchable, jackscrew or hydraulic mechanism, when specified in the Data Sheet.
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 30 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 7.8 LIMIT STOPS Limit stops shall be provided for control of opening only and when specified. Limit stops shall be mechanical devices on the actuator. Bolts screwed in the body shall not be used as a limit stop. Limit stops shall be adjustable over the full stroke length from 10% opening, unless otherwise specified. All limit stops shall be with lock nut and tamper-proof. 7.9 VOLUME BOOSTERS Volume boosters may be needed to reduce the stroking time of the valve. Pressure boosters shall not be used to adjust pressure and get the same effect. Material shall be in SS 316L, unless otherwise specified. 7.10 LOCK UP RELAY / VALVE Lock-up pneumatic relay/ valve may be provided for locking up the valve in its closed position on air supply failure, as part of complete assembly for fail-safe valve action on air supply failure. Air lock relay shall be provided so that the SOV lies between air lock relay and input to actuator. The lock-up valve shall be set at 8 psi above the minimum required air supply pressure, unless otherwise specified. Lock-up valve setting shall be tamper proof. Lock-up valve shall be in SS 316L, unless otherwise specified. 7.11 QUICK EXHAUST VALVES Quick Exhaust air valve in SS 316L shall be pilot operated type and fitted with bug screen on vent. Quick Exhaust valve shall be of fail-safe design and PFD values shall be provided to achieve required **SIL** rating. Mounting shall be on a SS 316L plate along with other accessories required for stroking time adjustment. 7.12 RESTRICTORS Restrictors in SS 316L shall be lockable, adjustable (variable) restriction. The Restrictor shall only affect the stroking time to slow opening or slow closing and shall not influence other valve movement (repeatability, linearity or characteristic). Mounting shall be on a SS 316L plate along with other accessories required for stroking time adjustment. Direction of flow shall be marked on the body.
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 33 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 8. MATERIALS REQUIREMENTS Requirements given here are typical to serve as guideline. VENDOR to ensure that the proposed materials are suitable and corrosion/ abrasion resistant in respect of the service conditions specified in the data sheet. The material selection shall be as per the project Specification for Instrument Material selection (Doc. No. E1150-TS-2000-J-0010), Piping Material Specification (Doc. No. E1150-TS-2000-P-0001) and valve data sheet listed in section 4.3. All valve body and trim (wetted parts) materials shall be ASTM and UNS designated. Use of Aluminium, Cast iron or Ductile-iron is not acceptable. Carbon steel body with SS 316L trims or wetted parts for valves and equipment shall be provided as a minimum. Wetted parts materials shall comply with requirements of **NACE** MR01-75/ - ISO 15156, for sour service applications. For the other material of construction of the valve shall be as per the requirements of respective manual valve Piping Specifications (Ball or Butterfly) listed in section 4.3. Soft seal material shall be Viton, with other material selected based on service conditions specified in Data Sheet. The inner valve gaskets, if applicable, shall be non-asbestos suitable for the process fluids at specified maximum service conditions. Teflon Gaskets shall be used (as a minimum) with other material selected based on service conditions specified in Data Sheet. Actuator (air) diaphragm material shall be nylon reinforced neoprene or Buna-N rubber. However Buna N rubber shall not be used for valves on Instrument gas motive power. All metal accessories and auxiliaries shall be in SS 316L, unless otherwise specified. Air set shall be SS 316L and painted. Mounting plates, fasteners and fixtures shall be in corrosion resistant painted SS 316L. Use of SS 304 is prohibited. All fibre glass components should have Ultraviolet stabilizer agent to safeguard against solar radiation. Wherever galvanizing is done as a protecting method for structures, it should be done by hot dipping process only. 9. INSTALLATION / COMMISSIONING REQUIREMENTS When all the components / accessories are mounted inside the SS316L enclosure, the same shall be properly accessible and removable easily for replacement / maintenance. Shutdown Valves shall be installed in horizontal lines. However, VENDOR shall furnish permissible mounting arrangements in his manual. Certified and tested Lifting eyes for actuator shall be provided. VENDOR shall ensure that all items however small are installed, mounted and supported. No item shall be supplied loose for field mounting by others.
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 36 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 Welding procedures, performance of welders and welding operators shall meet the requirements of ASME B31.3. Certificates for castings shall include weld repair data including extent of repair, WPS, welder qualifications, post weld heat treatment and NDE following the repair(s). Repair welding shall be performed using a properly qualified and approved procedure. A repair procedure must include a method statement regarding the excavation, NDT, and welding requirements. The repair of major defects shall not be performed without the knowledge of the CONTRACTOR. Welding, NDE and heat treatment procedures require submittal and approval by the CONTRACTOR/ prior to affecting the repairs. NDT (as applicable) Magnetic particle test, Dye penetration test, Radiography or Ultrasonic examination shall be carried out for weld integrity/internal defects check and shall be as per the Piping Specifications identified in clause no. 4.3 of this specification. **NACE** Test (for Valves in sour service applications) Hardness test for wetted parts and any other test needed for compliance to **NACE** MR- 0175/ - ISO 15156 shall be provided as mentioned below. • Valve body and trim material shall be subjected to hardness test to ensure that the hardness requirements of **NACE** MR0175 / - ISO 15156 are met. • For small items (e.g. springs, pins, etc.) which cannot be hardness tested individually the VENDOR shall conduct tests on a random basis by selecting components from production runs or stores batches to ensure that the product complies fully with **NACE** MR0175 / - ISO 15156 requirements. • Hardness test shall be performed without damaging any component. Hydro-test (all valves) Hydrostatic test pressure shall be 1.5 times the MAWP at ambient temperature and there shall not be any visible leak during the test. The minimum test duration shall be 60 sec for body size 1" and below, 120 sec for body sizes from 2” to 8” and 180 sec for valve body size 10" and above. Hydro test for shell and packing shall be performed with actuator fitted. The Water quality shall be clean potable water, clear and free of sulphides, having below 30ppm chlorides and with temperature below 50°C. Valve shall be air dried after test. Pressure testing on cylinders shall be carried out for Hydraulic actuators and Pneumatic Piston/ Cylinder actuators to manufacturer’s standard. Requirements of Piping Specifications identified in clause no. 4.3 of this Specification shall also be met. Valve Seat leakage (all valves) Seat leakage class shall be Tight shutoff Rate A as per - ISO 5208 and as indicated in the Instrument Valve Data Sheet. Helium leak test (type test) for Hydrogen rich applications or N2 / Helium low temperature or cryogenic applications shall be performed only when specified in Data Sheet as a Type test or for EPA certification requirements.
ISO 5208 | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 36 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 Welding procedures, performance of welders and welding operators shall meet the requirements of ASME B31.3. Certificates for castings shall include weld repair data including extent of repair, WPS, welder qualifications, post weld heat treatment and NDE following the repair(s). Repair welding shall be performed using a properly qualified and approved procedure. A repair procedure must include a method statement regarding the excavation, NDT, and welding requirements. The repair of major defects shall not be performed without the knowledge of the CONTRACTOR. Welding, NDE and heat treatment procedures require submittal and approval by the CONTRACTOR/ prior to affecting the repairs. NDT (as applicable) Magnetic particle test, Dye penetration test, Radiography or Ultrasonic examination shall be carried out for weld integrity/internal defects check and shall be as per the Piping Specifications identified in clause no. 4.3 of this specification. **NACE** Test (for Valves in sour service applications) Hardness test for wetted parts and any other test needed for compliance to **NACE** MR- 0175/ - ISO 15156 shall be provided as mentioned below. • Valve body and trim material shall be subjected to hardness test to ensure that the hardness requirements of **NACE** MR0175 / - ISO 15156 are met. • For small items (e.g. springs, pins, etc.) which cannot be hardness tested individually the VENDOR shall conduct tests on a random basis by selecting components from production runs or stores batches to ensure that the product complies fully with **NACE** MR0175 / - ISO 15156 requirements. • Hardness test shall be performed without damaging any component. Hydro-test (all valves) Hydrostatic test pressure shall be 1.5 times the MAWP at ambient temperature and there shall not be any visible leak during the test. The minimum test duration shall be 60 sec for body size 1" and below, 120 sec for body sizes from 2” to 8” and 180 sec for valve body size 10" and above. Hydro test for shell and packing shall be performed with actuator fitted. The Water quality shall be clean potable water, clear and free of sulphides, having below 30ppm chlorides and with temperature below 50°C. Valve shall be air dried after test. Pressure testing on cylinders shall be carried out for Hydraulic actuators and Pneumatic Piston/ Cylinder actuators to manufacturer’s standard. Requirements of Piping Specifications identified in clause no. 4.3 of this Specification shall also be met. Valve Seat leakage (all valves) Seat leakage class shall be Tight shutoff Rate A as per ** - ISO 5208** and as indicated in the Instrument Valve Data Sheet. Helium leak test (type test) for Hydrogen rich applications or N2 / Helium low temperature or cryogenic applications shall be performed only when specified in Data Sheet as a Type test or for EPA certification requirements.
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 41 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 • Painting specifications • Impact on delivery for any stated custom technical requirements. • List of exceptions & Non-compliance list (mandatory). • List of spares, consumables, special tools, tackles and equipment (if any) for startup and Commissioning. • List of Spares, Consumables for 2-year operation spares (maintenance spares). • List of similar supply made in last five years. • Latest ISO-9001 certificate. • Sizing Calculations Sheet (Torque calculations for Actuator). • **SIL** Certificates/Report 18. VENDOR DESIGN DATA The VENDOR shall be responsible for supplying the data as specified in the VDRS. The following documents shall be supplied as a minimum for COMPANY’s information and use. The data shall be preferably on CD, properly indexed and readable like an e-Book. In such cases only one set of hardcopy of documentation would be needed. • Filled in Instrument Data Sheets in as per Project Format. • Torque calculations for Actuator & Valve. • Logic Schematics for Valve Actuation. • Wiring & Hook-up details schematic. • OEM catalogues and O&M manuals. • Outline/ General Arrangement Drawings with Bill of Material and Weight Data. • Material, Mill and Calibration Test Certificates. • IP & Hazardous Area Certificates. • Installation, Operational & Maintenance Procedure/ Manual. • Painting Procedure. • Fabrication and Quality Control Plan. • VENDOR Data Book • List of Spares, Consumables, Special tools and Equipment for Start-up and Commissioning. • List of Spares, Consumables for Two years operation. • Manufacturing Record Book. • Welding Procedure Specification. • Functional Safety Assessment Reports/ Failure Rate data, **SIL** Certificate, Safety Manual. • Response Time. • Guarantee/Warrantee. • FAT Procedure. • Calibration and Pressure Testing Procedure. • Calibration Report. • Start-up and Commissioning. • Manufacturing Schedule
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 42 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 • Fire Safety Certification • Pneumatic - Hydraulic Schematic • Inspection Test Plan • Fugitive Emission Test Procedure (As applicable) • Liquid Penetrant Test Procedure • Magnetic Particle Inspection Procedure and report • Positive Material Identification - PMI – Procedure • Pressure and Leak Test Procedure and Record • Radiography Test Procedure and report • Seat Leak Test Procedure and report • Lubrication requirements • Certificate of Compliance – Conformity • Name Plate Detail • Volume tanks calculations • PFD Average / **SIL** Report Calculation for the complete valve assembly (valve, actuator, components etc.) 19. APPENDICES Appendix-1A: Partial Stroke Testing Scheme for Pneumatic Single Acting Valve Appendix-1B: Partial Stroke Testing Scheme for Pneumatic Double Acting Valve
PMI | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR ACTUATED ON-OFF VALVES Company Doc No: E1150-TS-2000-J-0002 Rev.: C1 Page 42 of 47 Contractor/Eng Doc. No: 217601C-000-JSS-1543-0001 • Fire Safety Certification • Pneumatic - Hydraulic Schematic • Inspection Test Plan • Fugitive Emission Test Procedure (As applicable) • Liquid Penetrant Test Procedure • Magnetic Particle Inspection Procedure and report • Positive Material Identification - **PMI** – Procedure • Pressure and Leak Test Procedure and Record • Radiography Test Procedure and report • Seat Leak Test Procedure and report • Lubrication requirements • Certificate of Compliance – Conformity • Name Plate Detail • Volume tanks calculations • PFD Average / **SIL** Report Calculation for the complete valve assembly (valve, actuator, components etc.) 19. APPENDICES Appendix-1A: Partial Stroke Testing Scheme for Pneumatic Single Acting Valve Appendix-1B: Partial Stroke Testing Scheme for Pneumatic Double Acting Valve
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 5 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 7.8 TEMPERATURE INSTRUMENTS .......................... .......................................................... 50 7.9 VALVES (FOR CONTROL APPLICATIONS) ................................................................... 53 7.10 PRESSURE RELIEF DEVICES ................................................ ........................................ 58 7.11 MISCELLANEOUS FIELD INSTRUMENTS ..................................................................... 60 7.12 CONTROL PANELS & ASSOCIATED INSTRUMENTATION .......................................... 60 7.13 ANALYTICAL INSTRUMENTS ................................................. ........................................ 62 7.14 PACKAGE CONTROL SYSTEM ................................................. ..................................... 64 7.15 ROTATING MACHINE MONITORING SYSTEM (RMMS) ............................................... 65 7.16 FIRE AND GAS SYSTEMS (INCLUDING F&G DETECTORS) ....................................... 65 7.17 CONSTRUCTION DESIGN .................................................... .......................................... 66 7.18 INSTRUMENT BULK MATERIAL REQUIREMENTS ....................................................... 67 8. MATERIAL OF CONSTRUCTION (MOC) REQUIREMENTS ......................................... 71 9. INSTALLATION / COMMISSIONING REQUIREMENTS ................................................ 71 9.1 SPECIAL TOOLS ........................................................... ................................................... 71 9.2 START-UP & COMMISSIONING SPARES ...................................................................... 72 9.3 OPERATIONAL SPARES ...................................................... ........................................... 72 10. SURFACE PROTECTIVE COATING/ PAINTING ............................................................ 72 11. QUALITY ASSURANCE/ QUALITY CONTROL REQUIREMENTS ................................ 74 12. INSPECTION AND TESTING REQUIREMENTS ............................................................. 74 12.1 INTEGRATED TEST WITH ICSS SYSTEM ..................................................................... 76 12.2 INSTRUMENTATION AND CONTROL SYSTEM TESTING ............................................ 76 13. MARKING AND TRACEABILITY REQUIREMENTS ....................................................... 76 14. HANDLING, STORAGE, PRESERVATION AND PACKING REQUIREMENTS ............ 77 15. VENDOR DESIGN DATA ............................................................. .................................... 77 16. HAZOP AND **SIL** PARTICIPATION REQUIREMENTS: .................................................. 78 16.1 HAZOP: ................................................................................ ............................................. 78 16.2 **SIL** / LOPA ......................................................... ............................................................... 78 17. TRAINING ....................................................................... .................................................. 78 18. ATTACHMENTS .................................................................... ........................................... 79 18.1 ATTACHMENT 1: MAC INTERFACE TEMPLATES......................................................... 80
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 9 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 Acronym / Reference Description HAZOP Hazard and Operability HPT High Power Trunk IEC International Electro-technical Commission INE or IE Instrument Earth I/O Input/Output IS Intrinsic Safety ISA Instrument Society of America ISE Intrinsic Safety Earth ISO International Organization for Standardization LOPA Layer of Protection Analysis LCIE Laboratoire Central des Industries Electriques LCR Local Control Room MAC Main Automation Contractor MCC Motor Control Centre MOC Materials of Construction MTR Module Technical Room **NACE** National Association of Corrosion Engineers NC Normally Close NDT Non Destructive Testing NO Normally Open NPT Nominal Pipe Thread OPC OLE (Object Linking and Embedding) for Process Control PC Personnel Computer P&ID Piping & Instrumentation Diagram PLC Programmable Logic Controller PRM Plant Resource Management PST Partial Stroke Test
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 10 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 Acronym / Reference Description PSU Power Supply Unit PO Purchase Order PVC Poly Vinyl Chloride QA/QC Quality Assurance/Quality Control RFI Radio Frequency Interference RMMS Rotating Machine Monitoring System RTD Resistance Temperature Detector RTU Remote Terminal Unit SAT Site Acceptance Test SE Safety Earth SIF Safety Instrumented Function **SIL** Safety Integrity Level SIS Safety Instrumented System SOV Solenoid Operated Valve SPDT Single Pole Double Throw SPIR Spare Parts Inter-Changeability Record TCP/IP Transmission Control Protocol / Internet Protocol TSO Tight Shut-Off TUV Technischer Ueberwachungs Verein UAAI Umm Al Anbar Island UCP Unit Control Panel UHF Ultra High Frequency UL Underwriters Laboratories UPS Uninterrupted Power Supply UV Ultraviolet VDRL Vendor Document Requirement List VHF Very High Frequency
ISO 5208 | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 12 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 4.2 REFERENCE CODE AND STANDARDS 4.2.1 International Standards Organization (ISO) CODE TITLE - ISO 5167 Measurement of fluid flow by means of Pressure Differential Devices inserted in circular cross section conduits running full ISO-9001 Quality Management System - Requirements - ISO 15848 Industrial Valves- Measurement, test and qualification procedures for fugitive emissions. ** - ISO 5208** Industrial Valves- Pressure testing of metallic valves 4.2.2 International Society of Automation (ISA) CODE TITLE ISA – S5 Series Instrumentation Symbols and Identification, Binary Logic Diagrams for Process operations, Graphic symbols and Instrument Loop Diagrams. ISA S 18.1 Standard for Annunciator Sequences and Specifications ISA S20 Specification forms for Process Measurements & Control Instruments, Primary Elements & Control Valves ISA 75 Series Standards & Practices for Control Valves 4.2.3 American Petroleum Institute (API) CODE TITLE API 520 Part - I Sizing, Selection and Inst. of Pressure Relieving devices in Refineries – Sizing and Selection API 520 Part- II Sizing, Selection and Inst. of Pressure Relieving devices in Refineries – Installation API STD 521 Guide to Pressure Relieving and Depressurization Systems API STD 526 Flanged Steel Pressure Relief Valves API STD 527 Seat tightness for Pressure Relief Valves API RP-551 Process Measurement Instrumentation
PMI | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 13 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 CODE TITLE API RP-552 Transmission Systems API RP-555 Process Analyzers API 578 Positive Material Identification (**PMI**) API STD 607 Fire Test for Soft Seated Quarter Turn Valves API STD 609 Butterfly Valve: Double Flanged, Lug and Wafer Type API 6FA Specification for Fire Test of Valves API 670 Machinery Protection System API 682 Pumps-Shaft sealing systems for Centrifugal & Rotary pumps API 576 Inspection of Pressure relieving devices API 598 Valve inspection & testing API 6D Specification for Valves (Gate, Ball, Check) 4.2.4 American Society of Mechanical Engineers (ASME) CODE TITLE ASME B 1.20.1 Pipe Threads, General Purpose (Inch) ASME B 16.5 Pipe Flanges and Flanged Fittings NPS ½ Through NPS 24 Metric/Inch Standard ASME B16.36 Orifice Flanges ASME B31.1/B31.3 Power and Process Piping Package ASME B40.100 Pressure Gauges and Gauge Attachments ASME B40.200 Thermometers, Direct Reading and Remote Reading ASME PTC 19.3 Temperature Measurement Instruments and Apparatus (Performance Test Codes). ASME PTC 25 Performance Test Codes-Pressure Relief Devices ASME SEC VIII DIV 1 Boilers and Pressure Vessels Code – Rules for Construction of Pressure Vessels FCI 70-2 Fluid controls Institute – Quality control standard for Control valve seat leakage
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 16 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 CODE TITLE FF-593 HSE Redundancy FF-801 Network Management FF-803 HSE Network Management FF-816 31.25 kbit/s Physical Layer Profile Specification/FISCO FF-831 Fieldbus Power Supply Test Specification FF-844 H1 Cable Test Specification FF-870 Fieldbus Message Specification FF-880 H1 System Management FF-890 Function Block Application Process Part 1 FF-891 Function Block Application Process Part 2 (10 Standard FBs) FF-892 Function Block Application Process Part 3 (Advanced FBs) FF-893 Function Block Application Process Part 4 (Multiple I/O FBs) FF-894 Function Block Application Process Part 5 (Flexible FBs) FF-900 Device Descriptor Language FF-902 Transducer Block Common Structure FF-903/904/906/908 Transducer Block Application Process Part 2 (Details Profile) FF-940 Communication Profile FF-941 HSE Profile RELCOM Foundation Fieldbus Wiring Design & Installation Guide 4.2.8 National Association of Corrosion Engineers (**NACE**) CODE TITLE **NACE** MR-0175 / - ISO 15156 Petroleum and Natural Gas industries- Materials for use in H2S containing environments in Oil and Gas Production.
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 21 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 Function of the local panel, if any, shall be limited to local indicators and emergency push buttons without any logic units/devices installed in the field. In this type of Package, all the instruments and accessories within the package skid shall be supplied, installed, wired and terminated in the junction boxes supplied and mounted on the skid or local panel by the Package VENDOR. Multi pair/triad cables between the Package VENDOR supplied local panels/ junction boxes and the Unit Control Panel located in the Local Control Room/Module Technical Room shall be by the EPC CONTRACTOR. d) Package Type D Type D Packages shall be fully operated by Local Control Panel in the field, with serial/hardwired link to the Island BPCS, hardwired link to SIS and FGS. Redundant CPU with applicable redundant IO Modules need to be considered. Safety loops shall be redundant Safety IO modules. In this type of Package, all the instruments and accessories within the package skid shall be supplied, installed, wired and terminated in the Local Control Panel. Multi pair/triad cables between the Package Vendor supplied Local Control Panel and the Island BPCS, SIS & FGS located in the Local Control Room/Module Technical Room shall be by the EPC CONTRACTOR. As far as practical, package control systems shall be implemented in Yokogawa STARDOM PLC for non-**SIL** applications, in Yokogawa Prosafe RS PLC in case of **SIL** (SIS and FGS) applications or in Siemens make PLC for control and safely function (**SIL**) application of package. The below table provides the list of the packages with Type for the “1 MMBD Expansion Phase 1 - Surface Facilities” project. This classification is in line with existing 750 philosophy and classification philosophy. Any deviation would need Company approval prior finalization. Sr. No. Package Description Interface Type Remarks Package Type A 2 Chemical Injection Package Not Applicable 4 Deaerator Package Not Applicable 5 Sea Water Fine Filtration Package Not Applicable 6 Produced Water Treatment Package Not Applicable
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 28 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 (E1150-A3-2100-J-2009), Instrument Process hook-up Drawing-UAAI (E1150-A3-2300-J- 2009), Instrument Process hook-up Drawing-ASI (E1150-A3-2200-J-2009) for details. Notes: 1) For diaphragm seal, the seal is the instrument connection 2) Instrument drain/vent shall be strictly connected as per Instrument hook-up drawings and Piping and Instrumentation Diagram (P&ID). 3) Flanged end connection rating shall be 300# RF, as a minimum for Instruments mounted on Process equipment. 4) For pipe class with higher ratings, instrument connection size shall be as per piping material specifications as applicable. 5) The stand pipe connections to the equipment will be 3”. 6) The type of flange shall be in accordance to Piping Material Specifications (Doc. No. E1150-GD-2000-P-0001). 7) Threaded connections shall be avoided in sour service. 8) Threaded/ Welded connections shall be avoided in Lethal service 9) Instrument Impulse tubing shall be 12 mm O.D. , 0.89 mm minimum wall thickness, SS-316L. However, selection of materials shall be chosen based on process condition. Material for sour service shall comply with applicable COMPANY & **NACE** standards MR0175/ - ISO 15156. For lethal service and pipe class rating of 1500# and above, hard pipe (instead of impulse tubing) shall be used for hook-up of transmitters. 10) The Thermowell connection Size for line shall be 1 ½” NB OE 2” NB depending on the piping material specification for the line. Refer Piping design and construction standard (E1150-BD-2000-P-0002) and Piping Material specification (E1150-TS- 2000-P-0001) for details. 11) Diaphragm seals are required for level instruments in lethal, severely dirty, corrosive, hazardous fluids, or fouling service. Pressure instruments for measurement in non- clean applications including slurry, dirty, highly viscous fluid will use diaphragm seal type transmitters with flushing ring. 6.7 HAZARDOUS AREA AND ELECTRICAL SAFETY The protection for Classified Electrical Hazardous area shall be as per IEC-60079, unless Local Statutory Codes overrule. All the package unit field instruments shall be certified suitable for the hazardous area Zone 1, Gas Group IIB, Temperature Class T3, as a minimum at an ambient temperature of 55 °C. However, for packages with possible presence of Hydrogen, the field instruments shall be certified suitable for the hazardous area Zone 1, Gas Group IIC, Temperature Class T3 as a minimum at an ambient temperature of 55 °C. The method of hazardous area protection for Instruments and Control Equipment located in the field shall be as below:
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 37 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 • Control valves: 40- 70 % for linear characteristics and 30- 70 % for equal percentage Characteristics. All trips shall be alarmed. All trip alarms shall be preceded by a pre-alarm and shall be generated for operator intervention & remedial action. Pre-alarm and Trip alarm signals shall not be derived from the same primary device or instrument and shall not share a common process tap/ connection/ thermowell. Process control shall be derived from separate segregated instrumentation and process taps from trip signals. Grouping of alarm contacts as a Common Fault alarm may be permitted only for non- process & off line non-critical utility alarms (e.g. panel ventilation fan failure). IOP alarm shall be generated in the system in event of input open. The IOP settings for all analog transmitters shall be 3.8 mA (IOP-) and 20.5 mA (IOP+). Switches shall not be used and Transmitters shall be used wherever practicable. Approval shall be sought for switches on a case-to-case basis. All instruments shall be purchased from reputed manufacturers on the COMPANY approved Instrument & Telecom Vendor List with proven track record of installation in similar Oil & Gas industries. Make and model of the Instrumentation and Control items supplied by Package VENDOR shall be same as that of main plant as far as is practicable to optimize COMPANY’s Spares / inventory requirement and simplify maintenance operation. VENDOR shall obtain this information from the EPC CONTRACTOR. Any deviation from approved Vendor List shall be subject to COMPANY approval. The DD & CFF revisions of Foundation Fieldbus instruments supplied by Package Vendor shall be compatible with the existing HOST system. Package vendor shall laise with MAC to collect information on DD & CFF revisions to be provided. Control Instruments (i.e. connected to BPCS or Package Control System) shall not be used for SIS duties and vice versa. In case a particular process variable needs to be used both for control and protection functions, two separate transmitters shall be provided. All the Safety Instrumented Functions (SIFs) part of the packages shall be subject to Safety Integrity Level assessment. All Instruments (including valves and actuators) used in safety applications (SIF) shall be **SIL** certified by a third-party like TUV, EXIDA, etc. All necessary data required for **SIL** verification shall be provided by package VENDOR. All transmitters inside the package unit shall be HART or FF compatible and shall be connected to the AMS (PRM supplied by Yokogawa) for instrument asset health monitoring. Transmitter calibrated ranges shall be selected so that Alarm and Trip points are above 10% and below 90 % of the calibrated range.
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 41 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 Instrument Stand pipes shall be fabricated from 2” Schedule 10S SS 316/316L. The stands shall be of welded and bolted construction and painted after welding. Stand Base Plates shall be fabricated from SS 316L of at least 5 mm thickness and shall be suitable for either welding or bolting to structural steel. Bolting shall be through Teflon inserts at least 3mm thick to avoid dissimilar metal contact. The Painting shall follow the Specification for Internal and External Coating (Doc. No. E1150-TS-2000-W-0004). Over range protections for field instruments shall be at least 130% of full scale or the design whichever is the higher. Wireless device shall be provided for critical local gauges which are difficult to access (physically or for safety reasons) and those that require regular monitoring. These devices shall be able to transfer all the readings electronically. These wireless devices shall be connected to BPCS through existing Wireless Gateway. The Wireless Gateway connects Wireless HART networks and communicates to the BPCS via modbus TCP/IP. Integration of wireless devices to wireless Gateway shall be by EPC CONTRACTOR. Package Vendor shall include all necessary provision in their design for critical local gauges if any identified as part of Package scope and provide complete support to EPC CONTRACTOR for integration of same with existing Wireless gateway. Instrument materials of construction shall be suitable for the process fluid and conditions and shall be selected based on the applicable Pipe Class detailed under the Project Piping Material Specification document (E1150-TS-2000-P-0001) and Specification for Instrument Material Selection (Doc. No. E1150-TS-2000-J-0010). The Process wetted parts/Trim Material shall be SS316L as a minimum or superior, as required for the application. All Field Instruments except in-line instruments shall be provided with the capability of being tested and calibrated In-Situ. All the field instruments including valves and accessories in hydrocarbon services shall conform to the requirements of **NACE** Standards MR-0175/ISO15156 (latest edition). 7.3 INSTRUMENT SELECTION Package VENDOR shall select all types of Instruments and valves for control application as per Instrument & Control Design Basis (Doc. No. E1150-BD-2000-J-0001), relevant Project specifications and warrantee/guarantees based on the minimum requirements indicated below. Package VENDOR shall submit an individual data sheet for each instrument & valve by tag within his supply in a .isf data sheet format provided by EPC CONTRACTOR. Separate instruments/sensors shall be provided for BPCS and SIS. Package VENDOR shall submit all the instrument datasheets for EPC CONTRACTOR/ COMPANY Review and Approval before PO placement to respective OEM. Any deviation from this specification and relevant project specifications shall be clearly highlighted for EPC CONTRATOR/COMPANY review and Approval.
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 54 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 All Valves in hydrocarbon service shall meet **NACE** MR 0175/ - ISO 15156. Unless otherwise specified all valves shall have ANSI valve seat leakage class- IV as a minimum. Sandwich type flangeless valve body suitable for use between pipe flanges with long bolts shall not be used. Split body valves shall not be used. The direction of flow shall be clearly marked on valve body. Ball valves shall not be used for process control applications unless globe valves would not be suitable (e.g. throttling valves on very low ∆P applications or on fast acting on-off service).Camflex type valves (or equivalent design) are a good choice for zero leakage instead of butterfly types especially for relieving pressure to flare header applications. This has got a special design to get tight shutoff compared to other types of valves. All Isolation valves shall be Bi-directional and Tight Shut-Off / Zero leakage as indicated in respective valve datasheet. 7.9.2 Sizing, standards, and regulations The sizing for valves for control applications shall be traceable to ISA S75.01.01: Flow equations for sizing control valves or - IEC 60534-2-1. Face to face details shall be to ISA S75.08 or API 609 based on type of valve. Aerodynamic noise prediction shall be traceable to ISA S75.17. Hydro-test of control valves shall be traceable to ISA S75.19.01. Leakage class shall be as per ANSI/FCI 70.2. For all valves in hydrocarbon services, low leakage loaded packing systems designed to reduce fugitive emissions shall be provided. All Valves in hydrocarbon service (Sour service) shall be certified for Fugitive Emission Certification as per - ISO 15848 Part 1 & Part 2. External leakage of valve stem seals (or shaft) and body joints of Valves in the HC service (sour service) shall be covered. The applicable tightness class for the stem shall be as per Table-1 of - ISO 15848 Part-2 based on packing and sealing materials. The acceptance criteria shall be as follows: • Production testing shall be done for valves sizes 16” above for all pressure rating -1 valve for every lot of 15 valves – minimum 1 per size.
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 65 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 All Package Control System shall be provided with HMI (touch screen facilities). HMI philosophy shall be as per described in the Specification for Human Machine Interface (HMI) (Doc. No. E1150-TS-2000-J-0047). Package Unit HMI system displays shall be designed using the same design philosophies as the ICSS, so that they “look and feel” like the ICSS displays. All necessary package unit data shall be transmitted to the ICSS for display on the BPCS HMI and on OTS simulator for Operator training. The HMI graphics shall be developed as per Specification for Human Machine Interface (HMI) (Doc. No.E1150-TS-2000-J-0047). Mirroring of package unit HMI to MAC HMI shall be established and implemented. The graphics shall include system alarm page indicating status of the healthiness of the system components. All package Control Systems shall be provided with output overrides for all outputs to external equipment and systems for isolation and major OI of packages. The package vendor shall configure the start permissive flow chart graphics to verify individual permissive for ready to start. The first up alarm to identify the first trip initiator out of a set of input causes shall be configured in the package control system. Shutdown signals requiring target **SIL** shall be implemented in a **SIL** certified PLC by VENDOR. Any Inter-Trips between the package VENDOR SIS and the main Island SIS (as defined on the Cause and Effect Diagrams) shall be transmitted on Hardwired links. 7.15 ROTATING MACHINE MONITORING SYSTEM (RMMS) Rotating Machinery Monitoring System (RMMS) shall be provided to monitor and protect the critical rotating equipment in compliance to API 670. Refer to “Specification Machine Monitoring System (Doc. No. E1150-TS-2000-J-0038)” for the requirements. 7.16 FIRE AND GAS SYSTEMS (INCLUDING F&G DETECTORS) The Package Unit VENDOR shall supply and install Fire and Gas Detection Systems as defined in Fire and Gas Philosophies and Specifications. The Package Unit VENDOR shall submit data sheets for each type of detector and signaling device within his supply complete with location diagrams and all other relevant drawings and documentation to the EPC CONTRACTOR/COMPANY for review and approval. The EPC CONTRACTOR and the Package Unit VENDOR shall perform **SIL** assessment as per - IEC 61508 & 61511 and based on the **SIL** assigned shall design the F & G Detection system accordingly and verify that all assigned **SIL** and Risk Reduction targets are
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 69 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 The supplied Cable gland shall comply with detailed requirement specified in “Specification for Instrument Cable, Cable Glands and Junction Boxes” Doc. No. E1150-TS-2000-J- 0016”. 7.18.5 Impulse tubing and Tube fittings Tubing with double compression fittings up to ASME 900 rating. Piping (not tubing) shall be provided up to the instrument manifold for Lethal Service and class ASME 1500 and above ratings. Tube size shall be ½” O.D. * 0.065” wall thickness. Tubing fittings shall be double compression double-ferruled type of Inconel 625 or 6MO or UNS S31803 or Titanium based on application/service, except for sea water/fire water service. For sea water/fire water service, Monel 400 shall be used. All tubing, fittings, Instrument Valve and Instrument Manifold shall be compliant to **NACE** MR0175/ - ISO 15156 as a default unless otherwise specified in specified in package specification. The supplied Impulse tubing and tube fitting shall comply with detailed requirement specified in “Specification for Instrument Bulk Materials (Doc. No. E1150-TS-2000-J-0018). 7.18.6 Pneumatic Tubing and Tube fittings: Pneumatic tubing shall be UNS N08904 (904 L SS) as per ASTM B 677-9. Tubing fittings shall be double compression double-ferruled type of 6MO in accordance with ASTM A182 and ASTM A479. Tube size will be specified as follows: • ¼ O.D. * 0.035” wall thickness – for small pilots (e.g. Transmitters). • 3/8 “O.D. * 0.035” wall thickness – for medium pilots (e.g. Control valves). • ½” O.D. * 0.049” wall thickness – for large pilots (e.g. Positioners). The supplied pneumatic tubing and tube fittings shall comply with detailed requirement specified in “Specification for Instrument Bulk Materials (Doc. No. E1150-TS-2000-J- 0018)”. 7.18.7 Instrument Air Supply Sets Instrument Air Supply Air sets (1/4” or ½”) shall be provided with integral filter, regulator and gauges. The Filter shall be of SS 316L to 40 micron as standard, unless otherwise specified. Instrument air take off points from plant instrument header shall be provided with isolation valves and spare ones shall be plugged. Instrument air up to instrument air manifold shall be supplied through SS 316L piping as per pipe class A51E of “Piping Material Specification” (Doc. No. E1150-GD-2000-P-0001).
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 71 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 8. MATERIAL OF CONSTRUCTION (MOC) REQUIREMENTS Material selection for Instrumentation shall be as follows: The selection of wetted parts and body material for in-line and on-line instrumentation and valves shall be in accordance with the “Piping Material Specification” (Doc. No. E1150-TS- 2000-P-0001) and Specification for Instrument Material Selection (Doc. No. E1150-TS- 2000-J-0010). The following shall apply for Material Selection for Instrumentation, as a minimum, unless otherwise specified. • All wetted parts shall be to SS 316L for process and utility services, as a minimum. This shall apply to all accessories too. Note: Monel wetted parts shall be used for seawater/fire water applications. • Capillary tubing shall be 316 L SS with protective armour in SS, as a minimum. • All wetted parts material of instruments in sour service shall comply with **NACE** MR 0175/ - ISO 15156. • Instrument Housing material shall be Low Copper Di-Cast Aluminium with epoxy painting or SS 316L, painted. • Use of SS 304 or lower grade and Aluminum is not permitted in any form. The sub-vendors, sub-suppliers and sub-contractors shall be selected from an Approved vendor list issued along with Project Requisition. 9. INSTALLATION / COMMISSIONING REQUIREMENTS The pre-commissioning and commissioning shall form part of site support services and the spares & consumables used during this stage by VENDOR shall be replenished free-of- cost to EPC CONTRACTOR/COMPANY, at the successful conclusion of commissioning services. 9.1 SPECIAL TOOLS SUPPLIER shall furnish, all special tools required for installation, commissioning, dis- assembly, and re-assembly of their equipment. These shall include but not limited to the following per equipment package. • Software (including any third-party software) configuration devices for all controllers, I/O modules. • Software (including any third-party software) for reconfiguration of operator interface.
NACE | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 75 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 A means to record/approve various stages of tests which shall allow testing from card/component/module level to total integration. As a minimum, the tests shall include the following activities or checks for Instruments or systems, as applicable. • Visual & Dimensional check. • Bill of material check. • Assembly checks. • Approved material for installation check. • Accessories completeness checks. • Mounting detail checks. • Material Test Certificates • Ratings check. • Leak checks. • NDT certificates check, when applicable. • **NACE** certificates check, when applicable. • Bench Calibration check. • Cabinets, wiring, trunking, termination, earthing etc. checks. • Electrical checks. • End connection checks. • Enclosure certification checks. • EMC certificate check. • Functional/ Performance /Operational check. • Input / Output (I/O) check including point / channel / module / system cable failure and reinstatement. • I/O points check for all types – analogue, contact, pulse, digital / discrete status flags etc. • Redundancy checks - Processor, Communication, Memory, Power supply and I/O, as applicable. • SWC test. • Common mode rejection ratio (CMRR) test for modules, when requested. • Time synchronization checks. • System Initialization checks. • Console checks and/or display checks for control loop configuration. • Software loading. • Logic checks with authorized issue of Cause and Effect or binary Logic diagrams. • Graphics check – Static and Dynamic. • Serial mapping check. • Auxiliary systems check –Maintenance PC etc. • Master – Slave controls check. • Supervisory system upload/download check. • Tagging, Cable numbering, termination ferruling and nameplate check.
SIL | PROJECT No. E1150 ENGINEERING, PROCUREMENT & CONSTRUCTION FOR 1.0 MMBD SUSTAIN PHASE 1 – SURFACE FACILITIES PROJECT SPECIFICATION FOR PACKAGE UNIT INSTRUMENTATION & CONTROL Company Doc No: E1150-TS-2000-J-0011 Rev.: C1 Page 78 of 90 Contractor/Eng Doc. No: 217601C-000-JSS-1580-0001 • Reliability and Availability Calculations. • System Architecture Diagram. • Hook-ups – Process, Electrical, Pneumatic, Hydraulic. • Wiring & Termination diagrams – Panel, Junction boxes and Termination boxes. • Interface diagrams. • Cable schedules. • Layouts – Process, Electrical, Pneumatic, Hydraulic. • Alarm and Trip settings list. • Modbus mapping and / or Serial link bit map. • I.S. Calculations. • Foundation Fieldbus Segment Design Calculations. • Certificates of conformity. • Enclosure certification including name plate drawing complete with Tag nos. and descriptions. • Electrical, Instrument air, instrument gas and analyzer calibration fluid consumption calculations, as applicable. • SPIR forms with Spares for commissioning and two-year Operational spares. • FAT and SAT procedures & Reports. • Application software for the equipment with licenses as required for use, including program and source codes as applicable. • Operating and Maintenance plans and manuals. • Sizing & Calculation books • Pre-commissioning procedures. • List of sub-orders /subcontracts from Package VENDOR. • At least Five- calibration points certificates for all instruments. 16. HAZOP AND **SIL** PARTICIPATION REQUIREMENTS: 16.1 HAZOP: Package VENDOR shall participate and assist EPC CONTRACTOR in HAZOP review meetings. Package VENDOR shall implement any HAZOP decisions and associated Package VENDOR design / documentation shall be revised accordingly. 16.2 **SIL** / LOPA **SIL** Assessments and LOPA reviews shall be carried out by EPC CONTRACTOR in compliance with the requirements of - IEC 61511. Package VENDOR shall participate in LOPA / **SIL** Study . 17. TRAINING Package VENDOR shall quote for training of various categories of instrument personnel necessary to maintain and troubleshoot Instruments and Control systems supplied by him. Such training shall preferably be imparted at site subsequent to installation of equipment at site and prior to commissioning. Trainings shall be in person at OEM’s facility or at Site
NACE | S.No. Rev No. COMMENT SECTION / CLAUSE / DRAWING REFERENCE / Page No. COMMENTED PERSON NAME DISCIPLINE COMPANY COMMENTS CONTRACTOR RESOLUTION COMPANY CONFIRMATION REMARKS 1 B Page no. 1 of 64 Sujay Ashok Piping 1) Actions provided in the minutes of meeting dated 07-Jun-2024 to be resolved prior to the next submission of PMS 2) Many streams in the MSD are missing. EPC to supply all the missing PFD to M&C SME to cover all the streams and allocate all the piping classes accordingly. same shall be listed in PMS 3) Wall thickness calculation , Reinforcement pad calculation report to be submitted prior to next submission of PMS for thickness validation. 4) For sizes above 24" thickness shall comply to clause 6 of this PMS 1) Noted and PMS is updated in line with MSR. 2) Noted,lines which are missing in the PFDs's and the related piping class's are updated. 3) Wall thickness calculation attached in related file. Reinforcement pad calculation is not required based on the project requirements and follwed the branch size as per the standard branch size table. 4) Noted & compiled. 2 B Page no. 1 of 64 Sujay Ashok Piping CONTRACTOR to compile and provide all the changes made from FEED PMS to the EPC stage PMS in revision table for necessary review and approval Noted and will be submitted. 3 B Page no. 1 of 64 Sujay Ashok Piping PMS was received on 7th june. however updated MSR was received on 19th june. The PMS is reviewed based on MSR rev B. However MSR rev B is under COMPANY review and not yet approved. Any changes in the MSR/MSD shall be updated in the PMS Noted and PMS is updated inline with MSR in discussion with company. 4 B Page no. 1 of 64 Sujay Ashok Piping Delete this statement Comments Incorporated. 5 B Page no. 3 of 64 Sujay Ashok Piping Add Previous comment not incorporated MSD to be added in hold list PID to be added Wall thickness calculation report including RF pad calculation report Noted Wall thickness calculation attached in related file. Reinforcement pad calculation is not required based on the project requirements and follwed the branch size as per the standard branch size table. 6 B Page no. 18 of 64 Sujay Ashok Piping These are shell standard drawings shall be prt of shell standards . shifty accordingly Comments Incorporated. 7 B Page no. 18 of 64 Sujay Ashok Piping Move **NACE** to international standards Comments Incorporated. 8 B Page no. 30 of 64 Sujay Ashok Piping remove Typical comment wherever applicable Comments Incorporated. 9 B Page no. 34 of 64 Sujay Ashok Piping delete this portion Comments Incorporated. 10 B Page no. 49 of 64 Sujay Ashok Piping As per MSR plant air has 3mm CA. piping class to be assigned accordingly Based on the FEED CA is 1.5mm and the same is followed for instrument & Plant Air to maintain the continuity for existing material. However the MSR shall be updated accordingly. 11 B Page no. 49 of 64 Sujay Ashok Piping Confrim 11432-Z required? Confirmed & not required as per the MSR and P&ID 12 B Page no. 49 of 64 Sujay Ashok Piping delete note 14 Add refer clause 6.1 typical comment Noted & comments incorporated 13 B Page no. 49 of 64 Sujay Ashok Piping revision lines shall be outside typical comment Noted & updated 14 B Page no. 49 of 64 Sujay Ashok Piping Updated MSR /MSD to be refereed to covered all the process and utility schemes. Piping classes summarry shall cover all the streams as per the project scope Noted & same will updated in next revision 15 B Page no. 49 of 64 Sujay Ashok Piping Refer to the FEED PMS. all applicable noted as mentioned in the FEED PMS to be updated in thos column typical comment comments incorporated 16 B Page no. 50 of 64 Sujay Ashok Piping 013411-Z required? Confirmed & not required as per the MSR and P&ID 17 B Page no. 50 of 64 Sujay Ashok Piping mention fluids comments incorporated 18 B Page no. 50 of 64 Sujay Ashok Piping Add U/G comments incorporated 19 B Page no. 50 of 64 Sujay Ashok Piping Add note 12 "Note-12" already mentioned in the note section 20 B Page no. 50 of 64 Sujay Ashok Piping FBE coated piping not applicable for potable water comments incorporated 21 B Page no. 51 of 64 Sujay Ashok Piping confirm 033844-X SDSS LT SOUR applicable? confirmed & not applicable for current project scope. 22 B Page no. 52 of 64 Sujay Ashok Piping confrim 061502-X LTCS required? confirmed & not applicable for current project scope. 23 B Page no. 52 of 64 Sujay Ashok Piping confrim 063842-X required? confirmed & not applicable for current project scope. 24 B Page no. 52 of 64 Sujay Ashok Piping 253461-Y, 251445-X? confirmed & not applicable for current project scope. 25 B Page no. 52 of 64 Sujay Ashok Piping As manifold M-120 and M-121 is fabricated from piping add the manifolds and its details in a seperate row Manifold M-120 & M-121 detail is mentioned in remarks section of corresponding Piping classes 26 B Page no. 53 of 64 Sujay Ashok Piping Also additionaly mention project document for GRE specification comments incorporated 27 B Page no. 53 of 64 Sujay Ashok Piping delete note 14 comments incorporated 28 B Page no. 55 of 64 Sujay Ashok Piping refer previous comment provided in previous sheet for additional piping class refer the corresponding responses. 29 B Page no. 59 of 64 Sujay Ashok Piping As per 30-99-12-3209 rev 2 Stem shall be made from forgings / bars . update material comments incorporated 30 B Page no. 60 of 64 Sujay Ashok Piping As per 30-99-12-3209 rev 2 Stem shall be made from forgings / bars . update material comments incorporated 31 B Page no. 63 of 64 Sujay Ashok Piping valve datasheets shall cover the details accordingly Noted 32 B Page no. 63 of 64 Sujay Ashok Piping this note is not required as hard facing is of different types based on trim material and is already mentioned in the valve material details table comments incorporated 33 B Class 011440-X, Page 2 of 13 Sujay Ashok Piping holds to be cleared typical comment throughout for the pms. Wall thickness calculation report with RF pad calculation report to be submitted prior to next revsion of PMS comments incorporated Wall thickness calculation attached in related file. Reinforcement pad calculation is not required based on the project requirements and follwed the branch size as per the standard branch size table. 34 B Class 011440-X, Page 13 of 13 Sujay Ashok Piping temperature instrument run size range shall be updated to the maximun of the piping sizes typical comment for full piping class size range is updated as per the Project requirements & Piping standard assembly drawings 35 B Class 011441-Z, Page 2 of 12 Sujay Ashok Piping keep this XS as per FEED PMS, check and update comments incorporated 36 B Class 013842-X, Page 2 of 12 Sujay Ashok Piping update S for all stainless steel material typical comment wherever applicable for stainless steel schedule numbers comments incorporated 37 B Class 016620-X, Page 8 of 13 Sujay Ashok Piping why cross? are these required as per the project scope. MESC numbers to be allocated accordingly. typical comment wherever applicable comments incorporated 38 B Class 016620-X, Page 13 of 13 Sujay Ashok Piping why 2 different branch sizes. shall be kept consistent for a particular piping spec updated as per the Project requirements & Piping standard assembly drawings 39 B Class 017011-X, Page 3 of 5 Sujay Ashok Piping Shall be Ethylene propylene rubber (EPDM) hardness 70+/-5 shore A as per the GRE SOW and PMS. update for all GRE comments incorporated 40 B Class 017011-Y, Page 5 of 10 Sujay Ashok Piping delete blank pages comments incorporated 41 B Class 017015-X, Page 2 of 10 Sujay Ashok Piping Add note :- Gasket material shall be suitable for potable water system comments incorporated 42 B Class 017020-X, Page 2 of 10 Sujay Ashok Piping Valves in U/G firewater system shall be UL Listed & FM approved with position indicator and extended stem (extended stem should be applicable for underground installations). comments incorporated Contract No.: 4700021779 COMMENT RESOLUTION SHEET Document No. & Rev : Document Title: Company Response EPC FOR SAHIL PHASE III DEVELOPMENT PROJECT PIPING MATERIAL SPECIFICATION P16093-30-99-12-1602 Rev-A Project No.: P16093 Transmittal Ref :EPC-AON-SDP-TR-OUT-0416 CODE 1 - No comments, work to proceed. CODE 2 - With minor Comments, work can proceed subject to incorporation of comments. CODE 3 - Major comments, work cannot proceed. CODE 4 - Exception comments, document for information only. Form No: P16093-30-99-90-1601 FM-05 Rev-C
HARDNESS TESTING | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 4 of 66 Project No.: P16093 Revision: B Page: 4 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public Table of Contents 1. INTRODUCTION ................................................................... ............................................................... 6 2. PURPOSE AND SCOPE .............................................................. ........................................................... 7 3. DEFINITIONS AND ABBREVIATIONS .................................................. .................................................. 7 3.1. DEFINITIONS .................................................................... ........................................................................ 7 3.2. ABBREVIATIONS .................................................................. ..................................................................... 8 3.3. UNITS OF MEASURES .............................................................. ................................................................ 13 4. REFERENCE DOCUMENTS ............................................................ ..................................................... 14 4.1. PROJECT DOCUMENTATION .......................................................... ............................................................ 14 4.1.1 Design basis and Philosophies ......................................... ............................................................. 17 4.2. COMPANY AND SHELL SPECIFICATIONS & STANDARDS ............................................................................... 17 4.2.1 COMPANY Specifications ................................................ .............................................................. 17 4.2.2 Shell DEP Specifications .............................................. .................................................................. 18 4.3. INTERNATIONAL CODE AND STANDARDS ............................................... ....................................................... 20 4.3.1 American Society of Mechanical Engineers (ASME) ...................................................................... 20 4.3.2 American Society of Testing Materials (ASTM) ............................................................................. 21 4.3.3 American Petroleum Institute (API) .................................... .......................................................... 22 4.3.4 British Standards ..................................................... ...................................................................... 23 4.3.5 ISO - International Organization for Standardization ................................................................... 24 4.3.6 MESC Standards ........................................................ .................................................................... 24 4.3.7 MSS-SP Standards ...................................................... ................................................................... 27 4.4. ORDER OF PRECEDENCE............................................................. ........................................................ 28 5. SELECTION OF PIPING CLASS/PIPING IDENTIFICATION ..................................................................... 28 5.1. PIPING CLASS NUMBERING ......................................................... .............................................................. 28 5.2. MESC ........................................................................... ....................................................................... 30 6. GENERAL REQUIREMENTS ........................................................... ..................................................... 30 6.1. POST WELD HEAT TREATMENT ....................................................... .......................................................... 31 7. GENERAL MATERIAL REQUIRMENTS ................................................... ............................................. 32 7.1. MATERIALS FOR SOUR SERVICE ..................................................... ............................................................ 33 7.2. **HARDNESS TESTING** ........................................................... ..................................................................... 33 8. CLADDING ....................................................................... ................................................................. 33 9. REQUIREMENTS FOR PIPE .......................................................... ...................................................... 34 9.1. GRE/ GRP PIPING ................................................................ ................................................................. 34 10. REQUIREMENTS FOR FITTINGS ...................................................... ................................................... 34 11. REQUIREMENTS FOR FLANGES ....................................................... .................................................. 35 12. SPECTACLE BLINDS, SPADES AND SPACERS ........................................... ........................................... 36 13. GASKETS......................................................................... .................................................................. 36 14. REQUIREMENTS FOR BOLTING ....................................................... .................................................. 38 15. REQUIREMENTS FOR VALVES ........................................................ ................................................... 38
NACE | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 12 of 66 Project No.: P16093 Revision: B Page: 12 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public LO : Lever Operated Lb : Pound LTCS : Low Temperature Carbon Steel MBOPD : Million Barrels Oil Per Day MESC : Material & Equipment Standards & Codes MOC : Material of Construction MSS SP : Manufacturers Standardisation Society-Standard Practice MT : Magnetic Particle Testing **NACE** : National Association of Corrosion Engineers NDE : Non-destructive Examination NPS : Nominal Pipe Size NPT : Nominal Pipe Thread OS&Y : Outside Screw and Yoke OD : Outside diamater PCD : Pitch circle diameter PE : Plain Ends PT : Dye-Penetrant Testing PTFE : Poly Tetra Fluoro-Ethylene PWHT : Post Weld Heat Treatment RB : Reduced Bore RF : Raised Face
NACE | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 20 of 66 Project No.: P16093 Revision: B Page: 20 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public Document Number Document Title DEP 31.40.20.39-Gen HDPE Pipeline and piping systems for oil field applications 4.3. International Code and Standards It is the CONTRACTOR’s responsibility to obtain and be familiar with all codes and standards so referenced in the relevant documentation. Requirements indicated in such codes and standards shall not supersede the requirements of this scope of work but shall be complementary. Document No. Document Title **NACE** MR0175/ - ISO 15156-1/ 2/ 3 Petroleum, Petrochemical and Natural Gas Industries- Material for use in H2S containing Environments in Oil & Gas production 4.3.1 American Society of Mechanical Engineers (ASME) Document No. Document Title ASME B31.3 Process Piping ASME B36.10M Welded and Seamless Wrought Steel Pipe ASME B36.19M Stainless Steel Pipe ASME B16.48 Line Blanks ASME B16.47 Large Diameter Steel Flanges NPS 26 through NPS 60 Metric/Inch Standard ASME B16.9 Factory-Made Wrought Buttwelding Fittings ASME B16.5 Pipe Flanges and Flanged Fittings NPS 1/2 through NPS 24 Metric/Inch Standard ASME B16.11 Forged Fittings, Socket-Welding and Threaded
NACE | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 25 of 66 Project No.: P16093 Revision: B Page: 25 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public Document No. Description SPE 74/002 Carbon Steel Pipe (Amend./Supp. to ASTM A 106) SPE 74/003 Carbon Steel Pipe (Amend./Supp. to ASTM A 672) SPE 74/004 Carbon Steel Pipe (Amend./Supp. to ASTM A 333) SPE 74/005 Carbon Steel Pipe (Amend./Supp. to ASTM A 671) SPE 74/008 Stainless Steel Pipe (Amend./Supp. to ASTM A312) SPE 74/009 Stainless Steel Pipe (Amend./Supp. to ASTM A358) SPE 74/014 Pipe, Duplex/Super Duplex Stainless Steel ASTM A 790 SPE 74/017 Pipe, Nickel – Copper Alloy ASTM B 165 SPE 74/019 Nickel alloy Pipe to ASTM B 423 SPE 74/026 Nickel alloy Pipe to ASTM B 444 SPE 74/125 Hydrogen Induced Cracking Sensitivity Test (Amend./Supp. to **NACE** SPE 76/030 Branch Outlets fittings to MSS SP-97 SPE 76/100 Flanges (Amend./Supp. to ASME B16.5) SPE 76/101 Flanges (Amend./Supp. to ASME B16.47) SPE 76/110 Fittings (Amend./Supp. to ASME B16.9)
NACE | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 31 of 66 Project No.: P16093 Revision: B Page: 31 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public specifications and data sheets. - Hydrotest pressure shall be 1.5 times of the pipe class specified rated pressure at ambient temperature. - Carbon / Alloy Steel and LTCS pipes, fittings shall be SMLS up to 24” NPS. Single straight seam welded fabricated pipes shall be used for larger sizes. - Where the required wall thickness is outside the standard wall thickness/schedules scope of ASME B36.10M, following wall thicknesses should be selected from below table for sizes larger than DN 600 (NPS 24) , in accordance with SHELL DEP 31.38.01.10. Millimeters 6.35 12.7 23.83 34 48 62 7.92 14.27 25.4 36 50 64 8.74 (1) 15.88 26.97 38 52 66 9.53 17.48 28.58 40 54 10.31 (1) 19.05 30.18 42 56 11.13 20.62 31.75 44 58 11.91 (1) 22.23 32 46.02 60 (1)- not acceptable for carbon steel 6.1. Post Weld Heat Treatment For carbon steel / LTCS piping in sour service, the requirement of **NACE** MR0175/ - ISO 15156 & DEP 39.01.10.12 shall be fulfilled for all the welds. Carbon steel/ LTCS pipe (including cladded pipes) exceeding 20.0mm wall thickness; PWHT shall be applicable in accordance to DEP 31.38.01.31.  Mild, intermediate and severe Sour Service: All equipment and pipework in Carbon steel/LTCS must be subject to a post weld heat treatment, irrespective of their thickness. The post weld heat treatment must be performed in accordance with the requirements of the design code even though the thickness of the material may be below the minimum value. Exemption of PWHT for carbon steel: The need for PWHT because of the mild or intermediate sour service on a piping system can be avoided; if the following requirements are met to the satisfaction of the Company:  Hardness values obtained during welding procedure qualification record are below 248 HV5.  Standard welding procedures for all pipework shall provide for a minimum of two passes.  The use of double sided welding on larger diameter pipe, internal sealing runs
NACE | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 33 of 66 Project No.: P16093 Revision: B Page: 33 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public CS / LTCS forgings shall be supplied in the normalized or normalized & tempered condition and in compliance to the additional requirement of applicable MESC SPE. Material of jack screw shall be austenitic stainless steel & shall have XYLAN 1070 or takecoat 1000 coating. Compressed Asbestos Fibre (CAF) and Man Made Mineral Fibres shall not be used. The use of compressed asbestos fibre gaskets as a jointing material in any valve packing of components is strictly prohibited. If graphite-based materials cannot be used, e.g. for product contamination reasons, PTFE-based materials shall be applied up to a maximum temperature of 150°C. Machined surfaces shall be subject to 100 % MPI / DPT as applicable. Cast/Ductile iron shall not be used. Carbon / Alloy Steel material shall comply with the requirements of SHELL DEP 31-38-01-10 and ASME B31.3 table 323.2.2A. Impact testing requirements shall be in accordance with applicable ASTM material specifications & SHELL MESC SPE specifications / SHELL DEP 30-10-02-31-Gen for piping materials. 7.1. Materials For Sour Service All piping materials shall be in full compliance with the “Corrosion Control and Materials Selection Philosophy” ES 30-99-00-0102”. Piping classes specified for sour service shall satisfy the **NACE** MR0175/ - ISO 15156 requirements with additional requirement of DEP & MESC Specifications. All chemical restrictions, carbon content, sulphur content, carbon equivalent shall be in accordance with the ES 30-99-00-0102 and the additional requirements for MESC Specification. All castings and forgings shall be in the normalized or normalized and tempered condition. 7.2. Hardness Testing The maximum hardness limit of 248 HV10 in the parent Carbon Steel material is acceptable provided the pipe manufacturer demonstrate through the weld ability tests that the hardness in the weld, the heat affected zone and the values within 0.5mm from the fusion line shall not exceed 248 HV10 (Carbon Steel Only). Hardness requirement shall be in compliance with the ES 30-99-00-0102. 8. CLADDING For pipe cladding refer to Shell DEP 31-40-20-32 (v42). For piping valves, CRA weld overlay cladding shall comply with the requirements of MESC SPE 77/313, in addition to the company standards. Cladding procedure shall be followed as per company standard ES 30-99-00-0102.
HARDNESS TESTING | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 33 of 66 Project No.: P16093 Revision: B Page: 33 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public CS / LTCS forgings shall be supplied in the normalized or normalized & tempered condition and in compliance to the additional requirement of applicable MESC SPE. Material of jack screw shall be austenitic stainless steel & shall have XYLAN 1070 or takecoat 1000 coating. Compressed Asbestos Fibre (CAF) and Man Made Mineral Fibres shall not be used. The use of compressed asbestos fibre gaskets as a jointing material in any valve packing of components is strictly prohibited. If graphite-based materials cannot be used, e.g. for product contamination reasons, PTFE-based materials shall be applied up to a maximum temperature of 150°C. Machined surfaces shall be subject to 100 % MPI / DPT as applicable. Cast/Ductile iron shall not be used. Carbon / Alloy Steel material shall comply with the requirements of SHELL DEP 31-38-01-10 and ASME B31.3 table 323.2.2A. Impact testing requirements shall be in accordance with applicable ASTM material specifications & SHELL MESC SPE specifications / SHELL DEP 30-10-02-31-Gen for piping materials. 7.1. Materials For Sour Service All piping materials shall be in full compliance with the “Corrosion Control and Materials Selection Philosophy” ES 30-99-00-0102”. Piping classes specified for sour service shall satisfy the **NACE** MR0175/ - ISO 15156 requirements with additional requirement of DEP & MESC Specifications. All chemical restrictions, carbon content, sulphur content, carbon equivalent shall be in accordance with the ES 30-99-00-0102 and the additional requirements for MESC Specification. All castings and forgings shall be in the normalized or normalized and tempered condition. 7.2. **HARDNESS TESTING** The maximum hardness limit of 248 HV10 in the parent Carbon Steel material is acceptable provided the pipe manufacturer demonstrate through the weld ability tests that the hardness in the weld, the heat affected zone and the values within 0.5mm from the fusion line shall not exceed 248 HV10 (Carbon Steel Only). Hardness requirement shall be in compliance with the ES 30-99-00-0102. 8. CLADDING For pipe cladding refer to Shell DEP 31-40-20-32 (v42). For piping valves, CRA weld overlay cladding shall comply with the requirements of MESC SPE 77/313, in addition to the company standards. Cladding procedure shall be followed as per company standard ES 30-99-00-0102.
TAT | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : C Project No. P16093 Agreement No. 4700021779 Page : 39 of 66 Project No.: P16093 Revision: B Page: 39 of 66 Document No.: 30-99-12-0602 Date: 05/06/2024 ADNOC Classification: Public are acceptable for instruments bridle connections however; the same arrangement shall not be used for piping draining assemblies. In either case, use of MONO flange slimline valves are not permitted. The integral DBB valve shall be of Ball-Needle-Ball valve assembly with following minimum bore ID: Header Size (DN) Inlet Flange Size (DN) Minimum Valve Body Size (DN) Minimum Bore ID (mm) Remarks DN 15 DN 15 DN 15 10 Applicable for Piping System DN 20 DN 20 DN 20 10 Applicable for Piping System DN 25/DN 40 DN 25/DN 40 DN 25 14 Applicable for Piping System DN 50 and Larger DN 50 DN 25 14 Applicable for Piping System All sizes For Pipeline DN50 DN 25 20 Applicable for Pipeline System All Valves bolts/nuts material shall be as per the bolts/nuts material as specified in the SHELL MESC. All valve bolts & nuts shall be coated with XYLAN 1070 OR TAKECOAT 1000. SHELL MESC SPE 77/300, shall be applicable for the valves design and qualification. In case of unavailability of valid **TAT** certificate, the testing/ Qualification requirements, as per SPE 77/300, shall be performed by the Vendor and be witnessed by the Company representative. The certification/ witnessing by SHELL inspector is waived. Inspection and test plan for piping valves shall be as per Company ES 30-99-12-0030. Corrosion allowance shall be taken into account for all valves design and manufacturing. Valve data sheet must include corrosion allowance for all type of valves. Wherever, trim material alloy 825/ 625/ SS 316 is specified for ball valves; ball material shall be of solid Alloy of same specified trim material for valve sizes DN≤100. Larger valve sizes DN ≥ 150, CS/ LTCS + Alloy 825/ 625/ SS 316 clad can be accepted for the valve ball material, as applicable from techno economic point of view. Surface safety valves (SSVs) and choke valves shall meet the ASME rating 900/1500/2500 requirement as per corresponding piping class for mating flange design, ensuring dimension matches with companion flange PCD and OD. All other design, testing etc. shall comply with API 6A requirements. All API 6A valves in sour service shall comply with PSL-3G requirements. Lip seal design shall be ensured for all the valves in sour service; however, in cases where through conduit valves are used they shall have lip seal arrangement regardless of fluid service.
NACE | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : B Project No. P16093 Agreement No. 4700021779 Page : 54 of 66 Security Code: 5 – Public ADNOC Classification: Public NOTES: General Notes  Material descriptions given above are generic only. For detailed MOC, refer Attachment 2,3 & applicable SHELL MESC description/data sheets for procurement purposes.  Design Code for Piping Classes to be in accordance with ASME B31.3.  For Instrument Hydraulic/Pneumatic Lines, refer to the Instrumentation Specification.  Material groups indicated are from ASME B16.5/B16.34.  For PWHT requirements section 8.1 to be followed.  NDE requirements will be in accordance with Shell DEP 31.38.01.31 unless otherwise stated here. o RT = Radiographic Testing, applicable to butt-welds only. o MT = Magnetic Particle Testing, applicable to fillet & branch welds. o PT = Dye Penetrant Testing, applicable to fillet & branch welds.  Piping class range including DN 600[NPS 24] & above design meets full vacuum at ambient condition. Specific Notes 1. All materials for Sour Service shall conform to **NACE** MR0175/ - ISO 15156 requirements. 2. For Carbon and Low Alloy Steel piping in Sour Service, the requirement of **NACE** MR0175 / - ISO 15156-2 Clause 7.3.3 shall be fulfilled for all welds. 3. For GRE Piping Company Doc. No. 30.99.12.0024 and - ISO 14692 shall be applicable and Project Doc. No. P16093-30-99-12-1627 Specification for GRE Pipe, Fittings and Flanges. 4. Screwed and glued connection shall be applicable for GRE piping sizes 6" and smaller, adhesive-bonded joints shall be applicable for larger piping sizes in accordance to SHELL DEP 31.40.10.19. 5. Mating flanges for X-Tree shall be RTJ in accordance with the requirements of API6A. 6. Specified SDSS materials shall have minimum 25% Cr & PREN>40 7. GRE Pipes shall be applicable for U/G piping services only. 8. Zinc shall be less than 16% for Al Br material. 9. This class is also applicable to Category-M fluids as defined in SHELL DEP 31.38.01.31. 10. Restrict to 60°C if Chlorides are present. Refer note in piping class for further limitations. 11. All instrument air Galvanized piping shall be of aboveground installation only. 12. Fire deluge terminology established for piping downstream deluge valve (normally no flow/empty). 13. For material group refer notes in the piping classes. 14. Deleted. 15. SS316/316L shall be dual certified
NACE | PIPING MATERIAL SPECIFICATION Document No. : P16093-30-99-12-1602 Rev : A Project No. P16093 Agreement No. 4700021779 Page : 64 of 66 Security Code: 5 – Public ADNOC Classification: Public NOTES: 1. General Notes  In addition to the above, all valves shall comply with the Engineering Standard ES-30.99.12.0030 and the applicable Specification requirements material, design, testing, inspection and certification.  Pressure testing in accordance with the valve applicable design code, engineering standard and respective SPE’s.  Fire safe test as per API 6FA.  Ball valves larger than 4” sizes shall be provided with grease injection for the valve stem and seats according to applicable MESC additional requirements and the engineering standard specification ES 30.99.12.3209.  Valves Bolt & Nut materials shall be as specified in the respective piping class or the referenced Shell MESC Data sheet whichever is more stringent. PEEK shall only be used up to 2500# rating.  SS316/316L shall be dual certified.  Valves sizes up to 4” NPS shall be made from forged material.  All Gate & Globe valves shall be OS & Y with rising stem design.  Unless required to comply with process for dissimilar check valve requirements, Swing Check Valve will not be used.  Fugitive emission tightness Class shall be "B", except for Category "D" fluids.  All Dual Plate Check valves and Butterfly valves are Solid lug type up to DN 150 sizes and flanged type both ends for sizes larger than DN 150.  Viton (AED type) material shall not be applicable for Sour service.  Butterfly valves shall not be used above 300# rating.  Corrosion allowance for valve body shall be as per applicable piping class.  All Ball valves in wet sour service shall have the following extra requirements: o The MOC for the upper and lower bearings shall be an equivalent trim material as minimum with PTFE coating. o Additional trunnion bearing protection shall be provided to prevent the accumulation of ingress in valve trunnion. o Valves shall be provided with sealant injection featuring grease injection as per the applicable MESC catalogue SPEs.  Globe valves closure member (disk/plug) / wetted parts shall have hard facing.  Metal-seated valves shall be hard faced on seat rings/ball/wedge. 2. Specific Notes 2.1 All materials shall conform to **NACE** MR0175/ - ISO 15156 latest edition. 2.2 Valves shall be metal seated. 2.3 Ball material shall be solid Alloy 825/ 625/ SS 316 for DN 100 and smaller sizes and CS + Alloy 825/ 625/ SS 316 cladded for DN 150 and larger sizes as per the respective pipe class trim material; as applicable. 2.4 Butterfly valves shall be triple eccentric tight shut off (TSO) design only for the hydrocarbon services use, and shall be concentric for water service in Class 150# only. 2.5 Seat pocket and sealing areas shall have min. 3mm SS316L weld overlay. 2.6 Seat pocket and sealing areas shall have alloy 825/625 3mm weld overlay as a minimum.
NACE | Class 031440-Z Page 2 of 6 Metric units ADNOC Classification: Internal Design limits Temperature (°C) 0 50 75 100 125 150 Pressure (Barg) DN 15-80 51.1 50.1 48.3 46.6 45.8 45.1 Notes - Design limits acc. to ASME B16.5 flange rating mat. grp 1.1 - For bending of pipe see DEP 31.38.01.31-Gen. - For basis of design see DEP 31.38.01.10-Gen. - Use of coated bolt sets should be considered when exposed to marine environments. - Piping class design meets full vacuum at ambient temperature condition - Monoflange slimline valves shall be selected for clean services only. - Monoflange valve assemblies are offered fitted with 1/2" BSP to either 1/2", 3/8" or 10mm. compression tube. fittings. In the assemblies as a default, the 1/2" compression tube fitting is listed. However, selection of relevant Monoflange valve assembly to be agreed with principal based on associated local instrument tube fitting. standard. - The use of red. bore ball valves is considered most economical. Use full bore ball valves only when necessary for process/operating requirements. - Piston type check valves (DN 15-40) [NPS 1/2-1-1/2] for horizontal mounting only - The choice of gate valves, swing type check valves vs triple eccentric butterfly valves, dual plate check valves shall be based upon total purchase and installation cost, as well as weight and space savings. Eccentric butterfly valves and dual plate check valves shall not be used in fouling or abrasive services. Table of schedules DN Schedule 20 XXS 25 XXS 300 XS 350 80 400 60 500 60 Branch connections 90 degrees Run size 20 25 300 350 400 500 500 N N B B B A 400 N N B B A 350 N N B A 300 N N A 25 M J 20 J Code Explanation of characters A Equal tee BW B Reducing tee BW J Equal Tee BW M Reducing tee BW N Branch fitting Carbon steel Sour, **NACE** Plant Class no. 031440-Z Consignee ASME rating CLASS 300 Engineered by Corrosion allowance 6 mm Principal Revision letter Contr. job no. Revision date Project no.
NACE | Class 031440-Z Page 3 of 6 Metric units ADNOC Classification: Internal COMPONENT MATERIAL DESCRIPTION (For full material description see relevant MESC buying description.) Pipe PIPE Pipe DN 15-600 ASTM A106-B Flanges BLFL Blind flange DN 15-600 ASTM A105 WNFL Weld Neck Flange, RF DN 15-600 ASTM A105 Fittings CAPB Cap bw DN 15-600 ASTM A234-WPB E45B Elbow 45 deg LR bw DN 15-600 ASTM A234-WPB E90B Elbow 90 deg LR bw DN 15-600 ASTM A234-WPB TEEB Tee equal bw DN 15-600 ASTM A234-WPB Reducing fittings RECB Reducer Concentric bw DN 20-600 ASTM A234-WPB REEB Reducer Eccentric bw DN 20-600 ASTM A234-WPB TERB Tee Rducing bw DN 20-600 ASTM A234-WPB Valves BTFF Ball valve trunn FB flgd DN 50-600 Body: ASTM A105/A216-WCB/WCC Trim: AISI 316, filled PTFE BTRF Ball valve trunn RB flgd DN 80-600 Body: ASTM A105/A216-WCB/WCC Trim: AISI 316, filled PTFE GLVF Globe valve flgd DN 15-50 Body: ASTM A105 Trim: AISI 316, Stellite GLVF Globe valve flgd DN 80-200 Body: ASTM A105/A216-WCB/WCC Trim: AISI 316, Stellite CHDF Check valve dual plate flgd DN 300-600 Body: ASTM A216 Gr. WCB, **NACE** Trim: ASTM 316 Hard Facing Seat CHVF Check valve flgd DN 15-50 Body: ASTM A105 Trim: AISI 316, Stellite CHVF Check valve flgd DN 80-600 Body: ASTM A105/A216-WCB/WCC Trim: AISI 316, Stellite Miscellaneous GKSW Gasket spiral wound DN 15-600 AISI 316 (L), Graphite CS centring-/SS inner ring STBT Stud bolt with nuts --- ASTM A193-B7/A194-2H Coated with Xylan 1070 or Takecoat 1000 Branch Fittings BN6P Branch Fitting Plain DN 40-600 ASTM A105 BN6F Branch Fitting Flanged DN 50-350 ASTM A105 BROP Branch outlet bw DN 400-600 ASTM A105 BR6B Branch outlet bw DN 450-600 ASTM A105
NACE | Class 031441-Y Page 3 of 5 Metric units ADNOC Classification: Internal COMPONENT MATERIAL DESCRIPTION (For full material description see relevant MESC buying description.) Pipe PIPE Pipe DN 15-80 ASTM A106-B Flanges BLFL Blind flange DN 15-80 ASTM A105 WNFL Weld Neck Flange, RF DN 15-80 ASTM A105 SBNF Spectacle blind DN 15-80 ASTM A516-60 Fittings E90B Elbow 90 deg LR bw DN 15-80 ASTM A234-WPB TEEB Tee equal bw DN 15-80 ASTM A234-WPB TERB Tee Reducing bw DN 15-80 ASTM A234-WPB Reducing fittings RECB Reducer Concentric bw DN 15-80 ASTM A234-WPB REEB Reducer Eccentric bw DN 15-80 ASTM A234-WPB Valves BALR Ball valve RB DN 50-80 Body: ASTM A216 Gr. WCB, **NACE** Trim: INCONEL 625, PTFE Seats BALF Ball valve FB DN 50-80 Body: ASTM A216 Gr. WCB, **NACE** Trim: INCONEL 625, PTFE Seats GATF Gate valve DN 15-40 Body: ASTM A105N, **NACE** Trim: INCONEL 625 Stellited GATF Gate valve DN 50-80 Body: ASTM A216 Gr. WCB, **NACE** Trim: INCONEL 625 Stellited CHDF Check valve dual plate Solid Wafer lug / flgd DN 15-40 Body: ASTM A105N, **NACE** Trim: INCONEL 625 Stellited CHVF Check valve dual flgd DN 50-80 Body: ASTM A216 Gr. WCB, **NACE** Trim: INCONEL 625 Stellited Miscellaneous GKSW Gasket spiral wound DN 15-80 AISI 316 (L), Graphite CS centring-/SS inner ring GKIK Insulating Gasket kit DN 15-80 (G-10/11) with 316 SS CORE, PTFE SS Pres Enrg Spirl Spring STBT Stud bolt with nuts --- ASTM A193-B7M/A194-2HM Branch Fittings BN3P Branch Fitting Plain (Nipolet) DN 40-80 ASTM A105 BNLF Branch Fitting Flanged (Nipolet Flanged) DN 40-80 ASTM A105
TAT | MANUAL VALVE SPECIFICATION Document No. : P16093-30-99-12-1604 Rev : 1 Project No. P16093 Agreement No. 4700021779 Page : 9 of 17 Security Code: 5 – Public ADNOC Classification: Public NDT : Non-Destructive Testing NPS : Nominal Pipe size OEM : Original Equipment Manufacture PDDL : Project Document Deliverable List P&ID : Piping and Instrumentation Diagram PFD : Process Flow Diagram QMS : Quality Management System QA : Quality Assurance QC : Quality Control RDS : Remote Degassing Station SSV : Surface safety valves **TAT** : Type acceptance test TBE : Technical Bid Evaluation TPI : Third Party Inspector TD : Technical Deviation VDDL : Vendor Document Deliverable List 4. REFERENCE DOCUMENTS 4.1. Project Documentation Document Number Document Title 16-99-93-0650 EPC Scope of Work for SAHIL PHASE III DEVELOPMENT PROJECT Note: The latest edition of the applicable Project documents shall be included with Revision Numbers.
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 7 of 47 Security Code: 3 - Confidential ADNOC Classification: Public MSS Manufacturers Standardization Society **NACE** National Association of Corrosion Engineers NDE Non-Destructive Examination Abbreviation Description NPS Nominal Pipe Size PQR Procedure Qualification Report RP Recommended Practice SDSS Super Duplex Stainless Steel SPE Specifications Document SS Stainless steel TSO Tight Shut Off UNS Unified Numbering System VDRL Vendor Document Requirement List VQRF Vendor Quality Requirement Form 4 References Codes, standards and specifications referred to in this document or in the Purchase Description, or in any referenced document, form a part of the requirements of this specification in the manner and to the extent specified. Latest Editions of each publication shall be used, together with any amendment /supplements/revisions thereto. Further EPC Contractor shall provide the reference of Project specific Piping Material Specification, Material selection report in the Material requisition over and above this document for the procurement of valves.
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 10 of 47 Security Code: 3 - Confidential ADNOC Classification: Public BS EN 12266 part 1 Industrial valves – Testing of valves. Part 1: Pressure tests, test procedures and acceptance criteria – Mandatory requirements (Superseded BS 6755-1) BS EN 12266 part 2 Industrial valves – Testing of valves. Part 2: Tests, test procedures and acceptance criteria – Supplementary requirements ( Superseded BS 6755- 2) BS EN 12288 Industrial valves – Copper Alloy Gate Valves ( Superseded BS 5154) BS EN - ISO 17292 Metal ball valves for petroleum, petrochemical and allied industries (superseded BS 5351) BS EN - ISO 15761 Steel gate, globe and check valves for sizes NPS 4” and smaller, for the petroleum and natural gas industries (superseded BS 5352) International Standardization Organization (ISO) - ISO 9001 Quality Management and Quality Assurance Standards Guidelines for Selection and Use - ISO 5208 Inspection & Testing of Valves - ISO 8501 Preparation of steel substrate before application of paints and related product – Visual assessment of surface cleanliness BS EN - ISO 10434 Bolted bonnet steel gate valves for the petroleum, petrochemical and allied industries (Superseded BS 1414) BS EN - ISO 10497 Testing of Valves – Fire Type Testing Requirements - ISO 15156 Part 1 to 3 Materials for Use in H2S Containing Environments in Oil And Gas Production ( **NACE** MR0175 ) BS EN - ISO 15848 part 1 Industrial valves – Measurement, test and qualification procedures for fugitive emissions – Part 1: Classification system and qualification procedures for type testing of valves BS EN - ISO 15848 part 2 Industrial valves – Measurement, test and qualification procedures for fugitive emissions – Part 2: Production acceptance test of valves BS EN - ISO 5208 Industrial Valves – Pressure Testing of Metallic Valves
ISO 5208 | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 10 of 47 Security Code: 3 - Confidential ADNOC Classification: Public BS EN 12266 part 1 Industrial valves – Testing of valves. Part 1: Pressure tests, test procedures and acceptance criteria – Mandatory requirements (Superseded BS 6755-1) BS EN 12266 part 2 Industrial valves – Testing of valves. Part 2: Tests, test procedures and acceptance criteria – Supplementary requirements ( Superseded BS 6755- 2) BS EN 12288 Industrial valves – Copper Alloy Gate Valves ( Superseded BS 5154) BS EN - ISO 17292 Metal ball valves for petroleum, petrochemical and allied industries (superseded BS 5351) BS EN - ISO 15761 Steel gate, globe and check valves for sizes NPS 4” and smaller, for the petroleum and natural gas industries (superseded BS 5352) International Standardization Organization (ISO) - ISO 9001 Quality Management and Quality Assurance Standards Guidelines for Selection and Use ** - ISO 5208** Inspection & Testing of Valves - ISO 8501 Preparation of steel substrate before application of paints and related product – Visual assessment of surface cleanliness BS EN - ISO 10434 Bolted bonnet steel gate valves for the petroleum, petrochemical and allied industries (Superseded BS 1414) BS EN - ISO 10497 Testing of Valves – Fire Type Testing Requirements - ISO 15156 Part 1 to 3 Materials for Use in H2S Containing Environments in Oil And Gas Production ( **NACE** MR0175 ) BS EN - ISO 15848 part 1 Industrial valves – Measurement, test and qualification procedures for fugitive emissions – Part 1: Classification system and qualification procedures for type testing of valves BS EN - ISO 15848 part 2 Industrial valves – Measurement, test and qualification procedures for fugitive emissions – Part 2: Production acceptance test of valves BS EN ** - ISO 5208** Industrial Valves – Pressure Testing of Metallic Valves
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 11 of 47 Security Code: 3 - Confidential ADNOC Classification: Public Manufacturer’s Standardization Society (MSS) MSS-SP-6 Standard Finishes for Contact Faces MSS-SP-9 Spot Facing for Bronze , Iron and Steel Flanges MSS- SP-25 Standard Marking System for Valves, Fittings, Flanges and Unions MSS-SP-44 Steel pipe line flanges MSS-SP-54 Quality standard for steel castings for valves, flanges & fittings and other piping component MSS-SP-55 Quality Standard (Visual Method) for Steel Castings for Valves MSS-SP-80 Bronze Gate, Globe, Angle and Check Valves MSS-SP-97 Integrally Reinforced Forged Branch Outlet Fittings-Socket Welding, Threaded and Butt Welding Ends Equipment and Material Users Association EEMUA -182 Specification for integral Block and bleed Valve Manifolds For Direct Connection to Pipe work National Association of Corrosion Engineers (**NACE**) MR 0175 / ISO/ 15516 Part 1 to 3 Petroleum and Natural Gas industries – Materials for use in H2S– Containing Environment in Oil and Gas Production TM 0177 Test Method: Testing of Metals for Resistance to Cracking at Ambient Temperature TM 0284 Evaluation of pipeline Steel and Pressure Vessel Steels for Resistant to Hydrogen Induced Cracking. SP-04-72 Method and controls to prevent in service environmental cracking of carbon steel weldment in corrosive refining environment.
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 16 of 47 Security Code: 3 - Confidential ADNOC Classification: Public 7 Materials Material of construction for valves shall be as specified in the respective data sheets and Project Piping Material Specification Document. Restriction in chemical composition including carbon content, carbon equivalent and other requirements shall be fully in compliance to Project Piping Material Specification Document and MESC SPE 77/302. 1. Steel produced for valves shall be produced either in an electric furnace or by basic oxygen process. 2. Material requiring impact testing shall be in accordance with ASME B 31.3, Para 323.3 and method of testing shall be in accordance with ASTM A 370 with additional requirements of MESC SPE 77/302. 3. All materials in contact with sour service shall, as a minimum, meet the requirements of **NACE** MR0175 / - ISO 15156 (latest edition), as specified in the MESC specifications and Project Piping Material Specification Document. 4. Austenitic & duplex stainless steel and Inconel material shall be solution annealed condition as per the relevant ASTM standard and MESC SPE 77/302 and amendments. Also, all stainless & duplex steel valves and valve components (including trim but excluding gaskets) shall be supplied in the pickled condition. 5. CS / LTCS forgings shall be fully killed fine grained and shall be supplied in the normalized or normalized & tempered condition with compliance to additional requirement of MESC SPE 77/302. 6. Cast iron material shall not be used. 7. Heat number for the castings or material specification for the forgings shall be permanently marked on the valve body. 8. Where pressure retaining parts have been specified as forged, substitution of castings is not permitted without prior approval by PURCHASER. 9. All bolts & nuts used in valves shall be coated either by TAKECOAT OR XYLAN1070 10. The material of construction of Lever / Hand Wheel shall be of Ductile Iron/ Malleable Iron/Cast steel. The Grey Flake Cast Iron shall not be used. 11. Spring material for ball valves shall be UNS 07718 and same spring material shall be used for Check valves wherever required. The hardness of spring material shall be in compliance to **NACE**- MR- 0175/ - ISO 15156
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 17 of 47 Security Code: 3 - Confidential ADNOC Classification: Public 12. Ball and through conduit gate valves seat housing & stem bearing area shall be weld overlay with material same as trim material. 13. Minimum thickness of weld overlay shall be 3.0mm as per the trim material in final machined condition (as specified in data sheet). 14. There shall be minimum hardness differential of 50 BHN between body and closure seating surfaces on stainless steel valves and 20 to 30 BHN for carbon steel valves. For sour service, all metal to metal seated valves, the maximum hardness of the body seats, body back seats and the closure (gate, wedge, disc, blade, etc.) seating surfaces shall be as per **NACE** MR- 0175/ - ISO 15156 and relevant MESC specifications. 15. Metal seated valves shall be hard faced on seat rings/ ball / wedge as specified in the valve data sheets/ piping material specification. However, other suitable hard facing may also be proposed along with the bid for COMPANY review/ approval. 16. ENP (Electro less Nickel plating) coating on carbon steel and stainless steel surfaces is no longer recommended for valve component to protect them from corrosion & hence not acceptable. 17. CRA material used in sour service shall comply with material requirements of **NACE** MR 0175/ - ISO 15156. 18. PWHT shall be performed after weld overlay to meet requirements for sour services as per **NACE** MR 0175/ - ISO 15156. 19. Bonnet gaskets for the valves shall be suitable for the service condition specified in the data sheets. 20. All process wetted and pressure containing parts formed from plate for sour service application shall be resistant to HIC and same shall be demonstrated. 21. Bonnet Gaskets shall have corrosion resistance equal, at least, to that of the body and bonnet materials. Asbestos shall not be used in any case. Bonnet and cover gaskets for copper alloy valves shall be no – graphite compressed synthetic fiber. 22. Where “PTFE” gaskets, stem seals, gland packing, etc., are specified, the material shall be virgin or glass fiber – reinforced polytetrafluoroethylene. All packing materials (Elastomers) shall be Anti – Decompression (AED) Type. 23. For the offered seal materials, SUPPLIER to furnish the maximum permissible
ISO 5208 | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 21 of 47 Security Code: 3 - Confidential ADNOC Classification: Public & anti- static devices test certificates shall be provided during/ & after bid for the offered valves. 31. The TSO (Tight Shut – Off) valves shall comply with seat leakage rates A & B of BS EN 12266-1 & 2 (Supersedes BS 6755 Part 1) and ** - ISO 5208** and shall comply with requirements of MESC SPE 77/100, 77/191. 32. Uni-directional valves, check valves or any valves within preferred flow direction where such design have been agreed with the PURCHASER shall have a direction arrow cast integral with the body. Where check valves have a limit on flow direction, or valve orientation, such details shall be provided to PURCHASER at the bid stage. 33. Stem design shall be blow out proof. The anti-blowout stem/body configuration shall be capable of withstanding the full internal pressure of the valve as per appropriate class. Stem retention by means of body/stem threads and packing gland are not acceptable. The stem retainer ring or collar shall be integral with the stem. 34. Valves shall be designed to operate freely after the stem has remained in one position for an extended period of service or till the next periodic maintenance. 35. NPS 6” & above valves shall be provided with a sealant injection system for stem and seats. Sealant connection shall incorporate an internal non return valve, giant button head; cover with vent holes which seals off the connection by plugging the sealant port. The sealant and grease injection system shall be suitable for injecting sealant / grease with the valve in operating condition. 36. Valves shall be provided with extended bonnet in accordance with MESC SPE 77/200 in the following cases: I. For valves having design temperature lower than -50°C. II. For valves having operating temperature lower than -30°C. 37. Ball, Gate, globe and butterfly valves in low temperature service having design temp in between -30°C & -50°C which will not be operated are the “Non Operable” valves and do not require bonnet extension. These valves shall be tested as per base standard and fugitive emission testing in accordance with MESC SPE 77/312. 38. Wherever corrosion allowance is specified in data sheets / Material Requisition, the
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 30 of 47 Security Code: 3 - Confidential ADNOC Classification: Public 14 Repair Welds 1. No weld repair to valve bodies shall be made without a written approval from COMPANY or its authorized inspector. Weld repair procedure and qualification test shall be submitted for COMPANY approval. The COMPANY reserves the right to refuse any weld repair. 2. Weld repairs are permissible for castings only. Defective cast valve bodies and bonnets may be repaired by welding in accordance with the provisions of their respective standards and subject to agreement by the COMPANY. 3. Welds or weld repairs shall be subjected to stress relief heat treatment and shall be certified. Austenitic stainless steel and Inconel material shall be in the annealed condition. All cases for valves in sour service shall be certified as per **NACE** MR 0175/ - ISO 15156. 4. The welding procedures and qualifications of the welding procedures and welders to be employed in making the repairs must be in accordance with ASTM A488 or ASME section IX. 5. For weld repair qualification the SUPPLIER/VENDOR shall carry out any heat treatment, NDE and Charpy impact testing appropriate to the material being repaired. 15 NDT Requirements & NDE Acceptance Criteria NDT and NDE acceptance shall be in accordance with MESC SPE 77/302, Project Piping Material Specification Document and Annexure VIII of Quality system requirement (Doc. no. EP 30-99-97-0006-1) 16 Quality Assurance / Quality Control The EPC CONTRACTOR / VENDOR shall operate a quality system to ensure that requirements of the DEP 82.00.10.10-Gen & - ISO 9001-2008 are achieved. All EPC CONTRACTOR / VENDOR and their SUB- VENDORS shall be certified to - ISO 9001- 2008 and shall submit a copy of their certification. The manufacturers shall identify in documents to its SUPPLIER and SUB- CONTRACTORS all applicable QA/QC requirements imposed by the
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 32 of 47 Security Code: 3 - Confidential ADNOC Classification: Public 8. SUPPLIER shall provide Purchaser data sheets completely filled against their requirements, stamped, signed and deviations clearly marked for acceptance during bid stage. Quotation without above shall not be considered for technical review and evaluation. 9. SUPPLIER shall submit the pressure temperature chart for all elastomer use in valves for COMPANY / Purchaser review during bid and post bid. 18 Inspection and Testing 1. All valves shall be tested in accordance with their applicable ASTM , ASME, MSS, BS codes/ standards and in accordance with **NACE** MR0175/ - ISO 15156 (where required for sour service), with additional requirements of MESC SPE 77/302 and SPE 77/303 as applicable. 2. All austenitic stainless steel forgings shall be 100% liquid penetrate examined as per ASTM A -182 supplementary requirements S5, with acceptance criteria to ASME B 16.34, ANNEX D. 3. Valves requiring “Extended Bonnet” shall meet all the requirements as stated in MESC SPE 77/200 in addition to design and testing requirements specified in base standard of the valve & specified MESC SPEs. 4. The scope of witnessing and certification for non-destructive and other inspection & testing shall as per the Project ITP (Inspection and Test Plan), Project Material Requisition and Annexure VIII of COMPANY Quality System requirement doc. no. 3099-97-0006-1. Inspection shall ensure compliance of technical documents requirements enclosed with Material Requisition. 5. SUPPLIER shall submit the detail ITP (based on Project ITP & Project MaterialRequisitions) in line with Annexure VIII of COMPANY Quality System requirement doc. no. 30-99-97-0006-1for COMPANY/PURCHASER review and approval. The Third Party Inspection requirements (if any) shall be indicated in ITP for COMPANY/PURCHASER approval. 6. SUPPLIER shall certify that the specified heat treatments have been correctly carried out wherever required. 7. SUPPLIER shall conduct hardness test on finished components to be used for sour services, to ensure that the hardness requirements of **NACE** MR0175 / ISO
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 33 of 47 Security Code: 3 - Confidential ADNOC Classification: Public 15156 are met. Where hardness values exceed **NACE** Standard acceptable values, the part shall be rejected. 8. Valve hydrostatic testing shall be as per BS EN 12266-1 & 2 (Supersedes BS 6755 Part 1) or API 598 as appropriate or as specified in the valve data sheets. However, the valve hydro test pressure shall be as per ASME B 16.34 based on Material Group and Class Rating. 9. New gaskets shall be installed in valve bonnet and cover joints that were opened for any reason during the course of testing. 10. Casting shall not be impregnated with sodium silicate or any other material to prevent leakage during pressure testing. 11. Any valve gland packing or stem seal that leaked during testing shall be replaced with new material following thorough drying of the gland and packing cavity. Shell and Seat hydrostatic testing shall then be repeated for these valves. 12. No gasket compounds shall be used on any flanged component other than a light application of either graphite and oil or light petroleum grease. 13. Testing of all valve components shall be performed, especially valve body cavities, shall be thoroughly dried prior to preparation for packing and shipment. All gaskets surfaces shall be thoroughly cleaned and dried prior to preparation for packing and shipment. 14. Fire safe test shall be as per BS EN - ISO 10497 (Supersedes BS 6755 Part 2) or API 6FA. All valves offered shall have qualified Fire test certification, details of which shall be available for PURCHASER review. The material of construction of valves in the certificate shall not be different/ vary from the material in data sheet. 15. Anti-static device test shall be as per BE EN 12266-1 & 2 (Supersedes BS 6755 Part 2. 16. All metal seated isolation valves (ball & gate) in gas service shall be subjected to high pressure pneumatic shell test in accordance with Para. 3.5 of API 598 at 110% of design pressure. SUPPLIER shall refer to fluid schedule for gas service requirements. 17. For ball, gate, globe and butterfly valves, for fluids with a fugitive emission tightness class A (HS), gland packing tolerances shall be in accordance with MESC SPE 77/208.
PMI | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 34 of 47 Security Code: 3 - Confidential ADNOC Classification: Public 18. Fugitive emission production testing as per MESC SPE 77/312 is applicable for supply of all valves. ADNOC Onshore may waive production testing, in either of the following cases:  The valve has successfully passed the fugitive emission prototype testing in accordance with - ISO 15848-1 and MESC SPE77/300. The test report shall not be older than 2 years.  Production testing has been carried out on the same valve type, design, pressure class, size, fugitive emission class and under the same test conditions, with consistent quality over the last 6 months. 19. SUPPLIER shall prepare a sampling plan for fugitive emission production testing in accordance with annexure-A of MESC SPE 77/312 for the total number of offered valves and shall submit it along with the offer. 20. When tight shut-off (TSO) requirement is specified then it shall comply with seat leakage rates A or B, in accordance with BS EN 12266-1 unless otherwise stated. 21. Positive Material Identification (**PMI**) shall be conducted for all SS / CRA material as stated in material / purchase requisition. 22. For material requirements, chemical composition, heat treatment, impact testing, corrosion testing, welding & hard facing and NDE requirements SUPPLIER shall refer to MESC SPE 77/302 & MESC SPE 77/303. 23. The selection of sample valve for various tests such as radiography, magnetic / liquid penetrant, fugitive emissions shall be by ADNOC Onshore / nominated inspector. 24. The Inspection & test plan must include scheduling of tests, scope of test, standard followed for test, acceptance criteria, Hold and witness points, checklists, spec of testing medium, cleaning procedure after the test, packing etc. inspection of cleanliness and the packing shall be considered as Hold & Witness points.
UT | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 38 of 47 Security Code: 3 - Confidential ADNOC Classification: Public Appendix – 1 : (Sample Data Sheets) Data Sheet No. - BA-25-9-001 BALL VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRM ATION GENERAL DATA 2 OR 3 PIECE SPLIT BODY, BOLTED BONNET, END ENTRY, BODY VALVE TYPE : CAVITY OVER PRESSURE SELF RELIEF SEAT DESIGN BALL VALVE VALVE SIZE RANGE : DN 50 TO DN 100 VALVE ASME CLASS/RATING : 2500 # VALVE PORT : REDUCED BORE VALVE SERVICE : INJECTION GAS (LEAN GAS) VALVE END CONFIGURATION : FLANGED RF , SMOOTH FINISH (Ra 3.2 to 6.3 m) PIPING CLASS : 251490-Y CORROSION ALLOWANCE : 3 MM DESIGN DESIGN PRESSURE FULL RATING DESIGN/ OPERATING TEMPERATURE -46 TO 90 0C : BI- DIRECTIONAL, FIRE SAFE, ANTI STATIC & BUBBLE TIGHT SHUT OFF VALVE DESIGN DESIGN TYPE VALVE OPERATION : GEAR OPERATED BALL SUPPORT : TRUNION MOUNTED BALL LOCKING FACILITY : REQUIRED STEM : ANTI BLOW OUT TYPE (NO CASTING) SEAT : SOFT SEATED, RENEWABLE TYPE STEM PACKING : RENEWABLE (NOTE 8) BONNET/COVER : BOLTED (NON EXTENDED) MATERIALS BODY : ASTM A 350 LF2 CL . 1 / ASTM A 352 GR. LCB/LCC COVER/BONNET / GLAND FLANGE : ASTM A 350 LF2 CL . 1/ ASTM A 352 GR. LCB/LCC BALL (SOLID) : AISI 316 (L) STEM / TRIM / GLAND RING : A 182 F316(L) PRIMARY SEAT RING : VIRGIN / FILLED PEEK SEAT POCKET & STEM SEALING AREAS MINIMUM 3 MM THK. AISI 316(L) WELD OVERLAY SPRINGS INCONEL 718 (ASTM B637 UNS N0. 7718) SEALS : LIP SEAL, PEEK ( AED TYPE) : CARBON FIBRE GRAPHITE/ PERFORMED COMP. GRAPHITE/VITON B OR GLAND /STEM PACKING EQUIVALENT (NOTE 6) SPIRAL WOUND, SS 316, GRPAHITE FILLED, CS CENTRING / ISS INNER GASKET : RING BOLTING : ASTM A320-L7M / ASTM A194-7M (NOTE 9) CODES AND STANDARDS / TESTING / CERTIFICATION DESIGN CODE : BS EN - ISO 14313/API 6D FACE TO FACE DIMENSIONS : BS EN - ISO 14313/API 6D /ASME B16.10 END CONFIGURATION / DIMENSIONS : ASME B 16.5 FIRE SAFE : API 6FA / API 607 /BS EN - ISO 10497 AS APPLICABLE AS PER FUGITIVE EMISSION LEAK DETECTION OF VALVES FUGITIVE EMISSION TIGHTNESS : SPE 77/312 , ENDURANCE CLASS B HYDROSTATIC TEST & PNEUMATIC TEST : API 598 / BS EN 12266 - 1 & 2 (BOTH MANDATORY) : SPECIFICATION FOR VALVES (DOC. NO. 11.99.12.0603) AND ADNOC Onshore NDT (MPI/DP/RADIOGRAPHY/ **UT** ETC.) INSPECTION CLASS I MATERIAL CERTIFICATION : BS EN 10204 TYPE 3.2 : SPECIFICATION FOR PAINTING ADNOC Onshore STD.( DOC.NO.30.99.37.0013 REV PAINTING 2)
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 39 of 47 Security Code: 3 - Confidential ADNOC Classification: Public MARKING ; MSS SP 25 & MESC SPE SPECIFICATIONS OTHER APPLICABLE PROJECT SPEC. : PIPING MATERIAL SPECIFICATION (DOC. NO. 11.99.12.0601) MANDATORY ADDITIONAL REQUIREMENTS (LATEST EDITION) MESC ,SPE 76/001, SPE 77/100, SPE 77/110, SPE 77/130 ,SPE 77/ 211, SPE 77/302, SPE 77/303, SPE 77/312, SPE 81/001, SPE 81/002, SPE 85/103, SPE 85/200, SPE 85/203 & SPE 85/204, MR 0-175/ - ISO 15156 BALL VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION NOTES: 1. THIS DATA SHEET SHALL BE READ INCONJUNCTION WITH THE ABOVE SPECIFIED PIPING MATERIAL SPECIFICATION AND SPECIFICATION FOR PIPING VALVES 2. VENDOR SHALL CONFIRM THE SUITABILITY OF MATERIALS WITH RESPECT TO SERVICE/TEMPERATURE SPECIFIED IN RESPECTIVE PIPING CLASSES. 3. THIS DATA SHEET SHALL BE COMPLETELY FILLED BY THE VENDOR, STAMPED, SIGNED AND DEVIATIONS CLEARLY MARKED FOR ACCEPTANCE. QUOTATION WITHOUT THIS DATA SHEET WILL NOT BE CONSIDERED FOR TECHNICAL REVIEW AND EVALUATION. 4. SHORT PATTERN VALVES SHALL NOT BE ACCEPTABLE AND VALVES SHALL BE PROVIDED WITH ANTISTATIC DEVICES. 5. VENDOR SHALL CONFIRM THAT THE CORROSION ALLOWANCES (MAX. OF ABOVE) ARE CONSIDERED IN THICKNESS CALCULATION OF CARBON STEEL PARTS (IN CONTACT WITH FLUID). 6. GRAPHITE BASED PACKING SHALL CONTAIN CORROSION INHIBITOR TO PREVENT OXIDATION OF THE STEM. 7. VALVES SHALL HAVE POSITION INDICATOR SHOWING OPEN AND CLOSE POSITIONS. 8. ELASTOMERIC SEALS SHALL BE ANTI-EXPLOSIVE DECOMPRESSION (AED) TYPE. 9. ALL BOLTS AND NUTS USED IN VALVES SHALL BE COATED EITHER BY TAKECOAT 1000 OR XYLAN 1070 10. LIFTING EYES & SUPPORT LUGS SHALL BE PROVIDED FOR VALVES WEIGHING 250 KGS AND ABOVE. 11. FOR FLANGED END VALVES, BODY & FLANGES SHALL BE INTEGRALLY CAST OR FORGED. 12. ALL MATERIALS SHALL COMPLY WITH REQUIREMENTS OF **NACE** MR 0175/ - ISO 15156. 13. FOR THE GIVEN TEMPERATURE IN THE DATA SHEET, VALVE SEAT INSERTS (SOFT) MATERIAL SHALL BE ABLE TO WITH STAND THE LIMITING PRESSURE INDICATED IN RATING TABLE OF ASME B 16.34. REDUCTION IN LIMITING PRESSURE OF VALVE DUE TO LIMITATION OF SEAT INSDERT MATERIAL IS NOT ACCEPTABLE. 14. VENDOR SHALL SUBMIT P-T RATING CHART OF SELECTED SEATS/SEALS COMPLYING WITH THE ABOVE AT THE TIME OF BID AS WELL AS POST ORDER. 15. TORQUE LIMITING DEVICE SHALL BE PROVIDED FOR GEAR OPERATED VALVES TO AVOID MALFUNCTIONING.
UT | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 40 of 47 Security Code: 3 - Confidential ADNOC Classification: Public Data Sheet No. - GA-15-1-001 GATE VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION GENERAL DATA VALVE TYPE : BOLTED BONNET, OS & Y TYPE GATE VALVE VALVE SIZE RANGE : DN 100 TO DN 250 VALVE ASME CLASS/RATING : 1500# VALVE SERVICE : INJECTION WATER (SOUR SERVICE) VALVE END CONFIGURATION : FLANGED (RF) , SMOOTH FINISH (Ra 3.2 to 6.3 m) PIPING CLASS : 151437-X CORROSION ALLOWANCE : 3 MM DESIGN DESIGN PRESSURE : FULL RATING DESIGN/OPERATING TEMPERATURE : 0 TO 150 0C/ 64 0C VALVE DESIGN : RISING STEM, NON RISING HAND WHEEL DESIGN TYPE VALVE OPERATION : GEAR OPERATED GATE / WEDGE : FLEXIBLE WEDGE LOCKING FACILITY : REQUIRED STEM : ANTI BLOW OUT TYPE (NO CASTING) SEAT / BACK SEAT : RENEWABLE /INTEGRAL STEM PACKING : RENEWABLE MATERIALS BODY : ASTM A105N / ASTM A 216 GR WCB/ WCC COVER/BONNET : ASTM A105N / ASTM A 216 GR WCB/ WCC GATE / WEDGE : INCONEL 625+ STELLITE 6 (NOTE 11) STEM : INCONEL 625 GLAND FOLLOWER/ BUSH : INCONEL 625 BODY SEAT RING : INCONEL 625 + STELLITE 6 BACK SEAT : STELLITE 6 SEAT POCKET & STEM SEALING AREAS MINIMUM 3 MM THK. INCONEL 625 WELD OVERLAY GLAND FLANGE : A105N : DIAGONAL BRAIDED GRAPHITE YARN/ PREFORMED COMP. GRAPHITE/ GLAND /STEM PACKING VITON B SPIRAL WOUND INCONEL 625, GRAPHITE FILLED, CS CENTRING/ GASKETS : INCONEL 625 INNER RING BOLTING : ASTM A193-B7M / ASTM A194-2HM (NOTE 10) CODES AND STANDARDS / TESTING / CERTIFICATION DESIGN CODE : BS EN - ISO 10434 (SUPERCEDES BS 1414)/API 6D FACE TO FACE DIMENSIONS : BS EN - ISO 10434 / ASME B16.10 END CONFIGURATION / DIMENSIONS : ASME B 16.5 FIRE SAFE : API 6FA / API 607 /BS EN - ISO 10497 AS APPLICABLE HYDROSTATIC TEST &AIR TEST : API 598 / BS EN 12266 - 1 & 2 (BOTH MANDATORY) AS PER FUGITIVE EMISSION LEAK DETECTION OF VALVES SPE 77/312, FUGITIVE EMISSION TIGHTNESS ENDURANCE CLASS B : PMS & SPECIFICATION FOR PIPING VALVES (DOC. NO. 12.99.12.0607 & NDT (MPI/DP/RADIOGRAPHY/ **UT** ETC.) 0608) AND ADNOC Onshore INSPECTION CLASS I MATERIAL CERTIFICATION : BS EN 10204 TYPE 3.2 PAINTING : SPECIFICATION FOR PAINTING ADNOC Onshore STD. (DOC. NO. 30.99.37.0013) MARKING ; MSS SP 25 & MESC SPE SPECIFICATIONS OTHER APPLICABLE PROJECT SPEC. : PIPING MATERIAL SPECIFICATION (DOC. NO. 12.99.12.0607)
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 41 of 47 Security Code: 3 - Confidential ADNOC Classification: Public MANDATORY ADDITIONAL REQUIREMENTS (LATEST EDITION) MESC , SPE 76/001, SPE 77/101, SPE77/102, SPE 77/161,SPE 77/302, SPE 77/303, SPE 77/312, SPE 81/001, SPE 81/002 SPE 85/103, SPE 85/200, SPE 85/203 & SPE 85/204, MR 0-175/ - ISO 15156 NOTES: THIS DATA SHEET SHALL BE READ INCONJUNCTION WITH THE PIPING MATERIAL SPECIFICATION (DOC. NO. 12.99.12.0607) AND 1. SPECIFICATION FOR PIPING VALVES (DOC. NO. 12.99.12.0608) GATE VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION 2. THIS DATA SHEET SHALL BE COMPLETELY FILLED BY THE VENDOR, STAMPED, SIGNED AND DEVIATIONS CLEARLY MARKED FOR ACCEPTANCE. QUOTATION WITHOUT THIS DATA SHEET WILL NOT BE CONSIDERED FOR TECHNICAL REVIEW AND EVALUATION. 3. VENDOR SHALL CONFIRM THE SUITABILITY OF MATERIALS WITH RESPECT TO SERVICE/TEMPERATURE SPECIFIED IN RESPECTIVE PIPING CLASS. 4. VENDOR SHALL CONFIRM THAT THE CORROSION ALLOWANCES (MAX. OF ABOVE) ARE CONSIDERED IN THICKNESS CALCULATION OF CARBON STEEL PARTS (IN CONTACT WITH FLUID). 5. GRAPHITE BASED PACKING SHALL CONTAIN CORROSION INHIBITOR TO PREVENT OXIDATION OF THE STEM. 6. VALVES SHALL HAVE POSITION INDICATOR SHOWING OPEN AND CLOSE POSITIONS. 7. FOR FLANGED END VALVES, BODY & FLANGES SHALL BE INTEGRALLY FORGED. SHORT PATTERN VALVES ARE NOT ACCEPTABLE. 8. ALL MATERIALS SHALL COMPLY WITH REQUIREMENTS OF **NACE** MR 0175/ - ISO 15156. 9. LIFTING EYES & SUPPORT LUGS SHALL BE PROVIDED FOR VALVES WEIGHING 250 KGS AND ABOVE. 10. ALL BOLTS AND NUTS USED IN VALVES SHALL BE COATED EITHER BY TAKECOAT OR XYLAN 1070 11. THE MATERIAL OF GATE/ WEDGE CAN BE CARBON STEEL + INCONEL 625 WELD OVERLAY FOR SIZES DN 150 AND ABOVE.
UT | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 42 of 47 Security Code: 3 - Confidential ADNOC Classification: Public Data Sheet No. - GL-25-9-001 GLOBE VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION Specification Requirement Vendor Confirmation GENERAL DATA VALVE TYPE : BOLTED BONNET, OS & Y TYPE GLOBE VALVE VALVE SIZE RANGE : DN 50 TO DN 80 VALVE ASME CLASS/RATING : 2500# VALVE SERVICE : INJECTION GAS (SOUR SERVICE) VALVE END CONFIGURATION : FLANGED (RF) , SMOOTH FINISH (Ra 3.2 to 6.3 m) PIPING CLASS : 251490-Y CORROSION ALLOWANCE : 3 MM DESIGN DESIGN PRESSURE : FULL RATING DESIGN TEMPERATURE : -46 TO 90 0C : RISING STEM, NON RISING HAND WHEEL DESIGN TYPE, , STRAIGHT VALVE DESIGN PATTERN VALVE OPERATION : HAND WHEEL OPERATED DISC : SWIVEL PLUG DISC TYPE LOCKING FACILITY : REQUIRED STEM : ANTI BLOW OUT TYPE (NO CASTING) SEAT / BACK SEAT : RENEWABLE / INTEGRAL STEM PACKING : RENEWABLE MATERIALS BODY : ASTM A352 LCB/LCC/A350 LF2 CL. 1 COVER/BONNET : ASTM A352 LCB/LCC/A350 LF2 CL. 1 DISC : AISI 316 (L) + STELLITE 6 STEM : ASTM A 182 F 316 (L) GLAND FOLLOWER/ BUSH : ASTM A 182 F 316 (L) BODY SEAT RING : AISI 316 (L) + STELLITE 6 BACK SEAT : AISI 316 (L) + STELLITE 6 GLAND FLANGE : ASTM A352 LCB/LCC/A350 LF2 CL. 1 SEAT POCKET & STEM SEALING AREAS MINIMUM 3 MM THK. AISI 316 (L) WELD OVERLAY + STELLITE 6 : CARBON FIBRE GRAPHITE/ PERFORMED COMP. GRAPHITE/VITON B OR GLAND /STEM PACKING EQUIVALENT (NOTE 4) : SPIRAL WOUND, SS 316, GRPAHITE FILLED, CS CENTRING / SS INNER GASKETS RING BOLTING : ASTM A 320-L7M / ASTM A194-7M (NOTE -9) CODES AND STANDARDS / TESTING / CERTIFICATION DESIGN CODE : BS EN 1873 FACE TO FACE DIMENSIONS : BS EN 1873 / ASME B16.10 END CONFIGURATION / DIMENSIONS : ASME B 16.5 FIRE SAFE : API 6FA / API 607 /BS EN - ISO 10497 AS APPLICABLE HYDROSTATIC TEST & AIR TEST : API 598 / BS EN 12266 - 1 & 2 (BOTH MANDATORY) AS PER FUGITIVE EMISSION LEAK DETECTION OF VALVES SPE 77/312, FUGITIVE EMISSION TIGHTNESS ENDURANCE CLASS B SPECIFICATION FOR PIPING VALVES (DOC. NO. 11.99.12.0603) NDT (MPI/DP/RADIOGRAPHY/ **UT** ETC.) : AND ADNOC Onshore INSPECTION CLASS I MATERIAL CERTIFICATION : BS EN 10204 TYPE 3.2 PAINTING : SPECIFICATION FOR PAINTING ADNOC Onshore STD. (DOC. NO. 30 99 37 0013)
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 43 of 47 Security Code: 3 - Confidential ADNOC Classification: Public MARKING ; MSS SP 25 & MESC SPE SPECIFICATIONS OTHER APPLICABLE PROJECT SPEC. : PIPING MATERIAL SPECIFICATION (DOC. NO. 11.99.12.0601) MANDATORY ADDITIONAL REQUIREMENTS (LATEST EDITION) MESC , SPE 76/001, SPE 77/101, SPE77/102, SPE77/103, SPE 77/161, SPE 77/303, SPE 77/303, SPE 77/312, SPE 81/001, SPE 81/002 SPE 85/103, SPE 85/200, SPE 85/203 & SPE 85/204, MR 0-175/ - ISO 15156 NOTES: THIS DATA SHEET SHALL BE READ INCONJUNCTION WITH THE ABOVE SPECIFIED PIPING MATERIAL SPECIFICATION AND 1. SPECIFICATION FOR PIPING VALVES THIS DATA SHEET SHALL BE COMPLETELY FILLED BY THE VENDOR, STAMPED, SIGNED AND DEVIATIONS CLEARLY MARKED FOR 2. ACCEPTANCE. QUOTATION WITHOUT THIS DATA SHEET WILL NOT BE CONSIDERED FOR TECHNICAL REVIEW AND EVALUATION. GLOBE VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION 3. VENDOR SHALL CONFIRM THE SUITABILITY OF MATERIALS WITH RESPECT TO SERVICE/TEMPERATURE SPECIFIED IN RESPECTIVE PIPING CLASS. 4. GRAPHITE BASED PACKING SHALL CONTAIN CORROSION INHIBITOR TO PREVENT OXIDATION OF THE STEM. 5. VALVES SHALL HAVE POSITION INDICATOR SHOWING OPEN AND CLOSE POSITIONS. 6. FOR FLANGED END VALVES, BODY & FLANGES SHALL BE INTEGRALLY FORGED. SHORT PATTERN VALVES ARE NOT ACCEPTABLE. 7. ALL MATERIALS SHALL COMPLY WITH REQUIREMENTS OF **NACE** MR 0175/ - ISO 15156. 8. LIFTING EYES & SUPPORT LUGS SHALL BE PROVIDED FOR VALVES WEIGHING 250 KGS AND ABOVE. 9. ALL BOLTS AND NUTS USED IN VALVES SHALL BE COATED EITHER BY TAKECOAT 1000 OR XYLAN 1070
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 44 of 47 Security Code: 3 - Confidential ADNOC Classification: Public Data Sheet No. – CH-25-1-001 CHECK VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION GENERAL DATA SWING CHECK , BOLTED COVER, UNI- DIRECTIONAL CHECK VALVE TYPE : VALVE VALVE SIZE RANGE : DN 80 to DN 250 VALVE ASME CLASS/RATING : 2500# VALVE SERVICE : INJECTION WATER (SOUR SERVICE) FLANGED TO ASME B 16.5 RAISED FACE SERRATED FINISH (Ra VALVE END CONFIGURATION : 3.2 to 6.3 m) PIPING CLASS : 251437-X CORROSION ALLOWANCE : 3 MM DESIGN DESIGN PRESSURE : FULL RATING DESIGN/OPERATING TEMPERATURE : 0 TO 150OC / 64 0C VALVE DESIGN : BOLTED COVER : SHALL BE SUITABLE FOR HORIZONTAL & VERTICAL VALVE INSTALLATION INSTALLATION CLOSURE MEMBER : SWING DISC SEAT RING : RENEWABLE TYPE OF PATTERN : STANDARD (RB) MATERIALS BODY : ASTM A105/ ASTM A 216 WCB/ WCC DISC : INCONEL 625 + STELLITE 6 BODY SEAT RING : INCONEL 625 + STELLITE 6 HINGE / STOP PIN : INCONEL 625 + STELLITE 6 SEAT POCKET AREAS MINIMUM 3 MM THK. INCONEL 625 WELD OVERLAY SPRINGS : INCONEL 718 (ASTM B637 UNS N07718) BOLTING : ASTM A193-B7M / ASTM A194-2HM (NOTE 12) CODES AND STANDARDS / TESTING / CERTIFICATION DESIGN CODE : API 6D / - ISO 14313 FACE TO FACE DIMENSIONS : API 6D / - ISO 14313/ ASME B16.10 FIRE SAFE : API 6FA / API 607 /BS EN - ISO 10497 AS APPLICABLE HYDROSTATIC TEST & AIR TEST (BOTH : API 598 / BS EN 12266 - 1 & 2 MANDATORY) SPECIFICATION FOR VALVES (DOC. NO. 12.99.12.0608) AND ADNOC Onshore NDT (MPI/DP/RADIOGRAPHY/ UT ETC.) : INSPECTION CLASS I MATERIAL CERTIFICATION : BS EN 10204 TYPE 3.2 PAINTING : SPECIFICATION FOR PAINTING (DOC. NO. 30.99.37.0013) MARKING ; MSS SP 25 & MESC SPE SPECIFICATIONS OTHER APPLICABLE PROJECT SPEC. : PIPING MATERIAL SPECIFICATION (DOC. NO. 12.99.12.0607) MANDATORY ADDITIONAL REQUIREMENTS (LATEST EDITION) MESC, SPE 76/001, SPE 77/160, SPE 77/104,SPE 77/132, SPE 77/302, SPE 77/303, SPE 77/312 , SPE 85/103, SPE 85/200, SPE 85/203., **NACE** MR 0-175/ - ISO 15156 NOTES: THIS DATA SHEET SHALL BE READ IN CONJUNCTION WITH THE PIPING MATERIAL SPECIFICATION (DOC. NO. 12.99.12.0607) AND SPECIFICATION 1. FOR VALVES (DOC. NO. 12.99.12.0608)
UT | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 44 of 47 Security Code: 3 - Confidential ADNOC Classification: Public Data Sheet No. – CH-25-1-001 CHECK VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION GENERAL DATA SWING CHECK , BOLTED COVER, UNI- DIRECTIONAL CHECK VALVE TYPE : VALVE VALVE SIZE RANGE : DN 80 to DN 250 VALVE ASME CLASS/RATING : 2500# VALVE SERVICE : INJECTION WATER (SOUR SERVICE) FLANGED TO ASME B 16.5 RAISED FACE SERRATED FINISH (Ra VALVE END CONFIGURATION : 3.2 to 6.3 m) PIPING CLASS : 251437-X CORROSION ALLOWANCE : 3 MM DESIGN DESIGN PRESSURE : FULL RATING DESIGN/OPERATING TEMPERATURE : 0 TO 150OC / 64 0C VALVE DESIGN : BOLTED COVER : SHALL BE SUITABLE FOR HORIZONTAL & VERTICAL VALVE INSTALLATION INSTALLATION CLOSURE MEMBER : SWING DISC SEAT RING : RENEWABLE TYPE OF PATTERN : STANDARD (RB) MATERIALS BODY : ASTM A105/ ASTM A 216 WCB/ WCC DISC : INCONEL 625 + STELLITE 6 BODY SEAT RING : INCONEL 625 + STELLITE 6 HINGE / STOP PIN : INCONEL 625 + STELLITE 6 SEAT POCKET AREAS MINIMUM 3 MM THK. INCONEL 625 WELD OVERLAY SPRINGS : INCONEL 718 (ASTM B637 UNS N07718) BOLTING : ASTM A193-B7M / ASTM A194-2HM (NOTE 12) CODES AND STANDARDS / TESTING / CERTIFICATION DESIGN CODE : API 6D / - ISO 14313 FACE TO FACE DIMENSIONS : API 6D / - ISO 14313/ ASME B16.10 FIRE SAFE : API 6FA / API 607 /BS EN - ISO 10497 AS APPLICABLE HYDROSTATIC TEST & AIR TEST (BOTH : API 598 / BS EN 12266 - 1 & 2 MANDATORY) SPECIFICATION FOR VALVES (DOC. NO. 12.99.12.0608) AND ADNOC Onshore NDT (MPI/DP/RADIOGRAPHY/ **UT** ETC.) : INSPECTION CLASS I MATERIAL CERTIFICATION : BS EN 10204 TYPE 3.2 PAINTING : SPECIFICATION FOR PAINTING (DOC. NO. 30.99.37.0013) MARKING ; MSS SP 25 & MESC SPE SPECIFICATIONS OTHER APPLICABLE PROJECT SPEC. : PIPING MATERIAL SPECIFICATION (DOC. NO. 12.99.12.0607) MANDATORY ADDITIONAL REQUIREMENTS (LATEST EDITION) MESC, SPE 76/001, SPE 77/160, SPE 77/104,SPE 77/132, SPE 77/302, SPE 77/303, SPE 77/312 , SPE 85/103, SPE 85/200, SPE 85/203., **NACE** MR 0-175/ - ISO 15156 NOTES: THIS DATA SHEET SHALL BE READ IN CONJUNCTION WITH THE PIPING MATERIAL SPECIFICATION (DOC. NO. 12.99.12.0607) AND SPECIFICATION 1. FOR VALVES (DOC. NO. 12.99.12.0608)
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 45 of 47 Security Code: 3 - Confidential ADNOC Classification: Public CHECK VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION 3. VENDOR SHALL CONFIRM THE SUITABILITY OF MATERIALS WITH RESPECT TO SERVICE/TEMPERATURE SPECIFIED IN RESPECTIVE PIPING CLASS. 4. VENDOR SHALL CONFIRM THAT THE CORROSION ALLOWANCES ARE CONSIDERED IN THICKNESS CALCULATION OF CARBON STEEL PARTS (IN CONTACT WITH FLUID). 5. VALVES SHALL HAVE MARK OF FLOW DIRECTION. 6. ALL MATERIALS SHALL COMPLY WITH REQUIREMENTS OF **NACE** MR 0175/ - ISO 15156. 7. FOR FLANGED END VALVES, BODY & FLANGES SHALL BE INTEGRALLY CAST OR FORGED. 8. VALVE MANUFACTURER SHALL SUBMIT TO PURCHASER TABLE OF COMPLIANCE WITH THE PURCHASER ORDER. 9. LIFTING EYES & SUPPORT LUGS SHALL BE PROVIDED FOR VALVES WIGHING 250 KGS AND ABOVE. 10. VALVE DISC SHALL BE DESIGNED TO PROVIDE SUITABLE CLEARANCE, IN ACCORDANCE WITH THE ASME CLASS RATING FOR THE VALVE AND INSIDE DIAMETER OF THE CONNECTING PIPE FLANGES. 12. ALL BOLTS AND NUTS USED IN VALVES SHALL BE COATED EITHER BY TAKECOAT OR XYLAN 1070 THIS DATA SHEET SHALL BE COMPLETELY FILLED BY THE VENDOR, STAMPED, SIGNED AND DEVIATIONS CLEARLY MARKED FOR ACCEPTANCE. 2. QUOTATION WITHOUT THIS DATA SHEET WILL NOT BE CONSIDERED FOR TECHNICAL REVIEW AND EVALUATION.
UT | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 46 of 47 Security Code: 3 - Confidential ADNOC Classification: Public Data Sheet No. - DBB-25-3-001 DBB VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION GENERAL DATA FULL BORE, INTEGRAL TYPE, DOUBLE BLOCK & BLEED VALVE, VALVE TYPE : TWO FULL BORE BALL VALVE FOR ISOLATION AND 1/2” GLOBE NEEDLE VALVE FOR BLEED. (NOTE-6) VALVE SIZE RANGE : DN 50 TO 50 VALVE ASME CLASS/RATING : 2500# VALVE SERVICE : INJECTION GAS (SOUR SERVICE) : PIPE END FLANGED (RF) (DN 50), SMOOTH FINISH (Ra 3.2 to 6.3 m) PIPING CLASS : 251490-Y CORROSION ALLOWANCE : 3MM (NOTE 8) DESIGN DESIGN PRESSURE : FULL RATING DESIGN / OPERATING TEMPERATURE -46 TO 90 0C BALL VALVES FOR PRIMARY & SECONDARY ISOLATION (BLOCK) VALVE DESIGN : AND DN15-GLOBE, NEEDLE TYPE VALVE FOR BLEED, ANTI STATIC FIRE SAFE DESIGN VALVE OPERATION : LEVER OPERATED : FULL BORE, FLOATING BALL, BI-DIRECTIONAL, TIGHT SHUT OFF BLOCK VALVES DESIGN BLEED VALVE : FULL BORE, ANTI TAMPER TYPE, GLOBE TYPE NEEDLE VALVE STEM : ANTI BLOW OUT TYPE (NO CASTING) SOFT SEATS FOR BALL VALVE & METAL SEATS FOR GLOBE BODY SEAT/ STEM SEAL : NEEDLE / RENEWAL TYPE, BODY CAVITY OVER PRESSURE SELF RELIEF SEAT DESIGN MATERIALS (BLOCK VALVES) BODY / COVER/BONNET/GLAND FLANGE : ASTM A182 F 316 BALL : AISI 316 (L) STEM/GLAND RING : ASTM A182 F 316 (L) SEAT POCKET & STEM SEALING AREAS : AISI 316 (L) + COATED WITH STELLITE 6 BODY SEAT RING : PEEK STEM SEALS : VITON B (AED TYPE) / GRAPHITE CARBON FIBRE GRAPHITE/ PERFORMED COMP. GRAPHITE/VITON GLAND PACKING : B OR EQUIVALENT (NOTE 5) MATERIALS (BLEED VALVE) BODY / COVER/BONNET : ASTM A182 F 316 DISC : AISI 316 (L) STEM /TRIM : ASTM A182 F 316 (L) + STEM SEALING AREA COATED WITH STELLITE 6 : CARBON FIBRE GRAPHITE/ PERFORMED COMP. GRAPHITE/VITON BOLTING : ASTM A320-L7M / ASTM A194-7M (NOTE 7) CODES AND STANDARDS / TESTING / CERTIFICATION EEMUA 182 / ASME B 16.34/ BS EN - ISO 17292/API 6D FOR BALL DESIGN CODE : VALVE & BS EN - ISO 15761 FOR NEEDLE VALVE AS APPLICABLE FACE TO FACE DIMENSIONS : MANUFACTURER’S STANDARD END CONFIGURATION / DIMENSIONS : ASME B 16.5 (FLANGED END) / B1.20.1 (THREADED END) FIRE SAFE : API 6FA / API 607 /BS EN - ISO 10497 AS APPLICABLE HYDROSTATIC TEST & AIR TEST : API 598 / BS EN 12266 – 1 & 2 SPECIFICATION FOR VALVES (DOC. NO. 11.99.12.0603) AND ADNOC Onshore NDT (MPI/DP/RADIOGRAPHY/ **UT** ETC ) : INSPECTION CALSS I MATERIAL CERTIFICATION : BS EN 10204 TYPE 3.2 PAINTING : SPECIFICATION FOR PAINTING (DOC. NO. 30.99.37.0013) MARKING ; MSS SP 25 & MESC SPE SPECIFICATIONS OTHER APPLICABLE PROJECT SPEC. : PIPING MATERIAL SPECIFICATION (DOC. NO. 11.99.12.0601) MANDATORY ADDITIONAL REQUIREMENTS (LATEST EDITION) MESC SPE 77/110, SPE 77/130, SPE 77/170, SPE 77/302, SPE 77/303, SPE 77/312, SPE 81/002, SPE 85/103, SPE 85/200, SPE 85/203 & SPE 85/204 NOTES: THIS DATA SHEET SHALL BE READ INCONJUNCTION WITH THE ABOVE SPECIFIED PIPING MATERIAL SPECIFICATION AND SPECIFICATION FOR PIPING VALVES
NACE | Technical Centre - Engineering Specification Specification for Piping Valves Document No. : 30-99-12-3209 Rev : 2 Project No. : MASTER Page : 47 of 47 Security Code: 3 - Confidential ADNOC Classification: Public 1. THIS DATA SHEET SHALL BE COMPLETELY FILLED BY THE VENDOR, DULY STAMPED & SIGNED AND DEVIATIONS CLEARLY MARKED FOR ACCEPTANCE. QUOTATION WITHOUT THIS DATA SHEET WILL NOT BE CONSIDERED FOR TECHNICAL REVIEW AND 2. VENDOR SHALL CONFIRM SUITABILITY OF MATERIALS WITH RESPECT TO SERVICE/TEMPERATURE SPECIFIED IN RESPECTIVE PIPING CLASS. DBB VALVE TAG NO. - As per MESC numbers of respective piping class DESCRIPTION SPECIFICATION REQUIREMENT VENDOR’S CONFIRMATION 3. THE DOUBLE BLOCK & BLEED ASSEMBLY SHALL HAVE THREE VALVES- PRIMARY ISOLATION, SECONDARY ISOLATION & BLEED VALVE, ALL INTEGRATED IN A SINGLE PIECE. THE HANDLES/ WRENCH POSITION OF PRIMARY ISOLATION & SECONDARY ISOLATION SHALL BE ON OPPOSITE BODY FACES. 4. VENDOR SHALL CONFIRM THAT THE CORROSION ALLOWANCES (MAX. OF ABOVE) ARE CONSIDERED IN THICKNESS CALCULATION OF CARBON STEEL PARTS (IN CONTACT WITH FLUID). VALVES SHALL HAVE POSITION INDICATOR SHOWING OPEN AND CLOSE POSITIONS. 5. GRAPHITE BASED PACKING SHALL CONTAIN CORROSION INHIBITOR TO PREVENT OXIDATION OF THE STEM. 6. VALVES SHALL BE ONE PIECE INTEGRALLY FORGED INCLUDING END FLANGE. ALL MATERIALS SHALL COMPLY WITH REQUIREMENTS OF **NACE** MR 0175/ - ISO 15156. 7. ALL BOLTS AND NUTS USED IN VALVES SHALL BE COATED EITHER BY TAKECOAT 1000 OR XYLAN 1070 8. THE SPECIFIED CORROSION ALLOWANCES SHALL NOT BE APPLICABLE, IF VALVE BODY MATERIAL WILL BE STAINLESS STEEL.
NACE | SPECIFICATION FOR ON OFF VALVES, SHUTDOWN VALVES AND BLOWDOWN VALVES Document No. : P16093-30-99-39-1604 Rev : 2 Project No. P16093 Agreement No. 4700021779 Page : 4 of 29 Security Code: 5 – Public ADNOC Classification: Public TABLE OF CONTENTS 1. INTRODUCTION ................................................................... .................................................................. 5 2. PURPOSE AND SCOPE .............................................................. .............................................................. 6 3. DEFINATIONS AND ABBREVIATIONS .................................................. ................................................... 6 3.1. DEFINITIONS .................................................................... ............................................................................ 6 3.2. ABBREVIATIONS .................................................................. ......................................................................... 7 4. REFERENCE DOCUMENTS ............................................................ ........................................................ 10 4.1. PROJECT DOCUMENTATION .......................................................... ................................................................ 10 4.1.1 Project Datasheets .................................................... ........................................................................ 10 4.1.2 Project Specifications ................................................ ........................................................................ 10 4.1.3 Design basis and Philosophies ......................................... ................................................................. 11 4.2. COMPANY AND SHELL SPECIFICATIONS & STANDARDS ................................... ................................................ 11 4.2.1. COMPANY SPECIFICATIONS ......................................................... ............................................................... 11 4.2.2. SHELL DEP VERSION 41 SPECIFICATIONS ............................................ .......................................................... 12 4.2.3. AGES ........................................................................... ........................................................................... 13 4.3. INTERNATIONAL CODES AND STANDARDS .............................................. .............................................. 14 4.3.1. AMERICAN SOCIETY OF MECHANICAL ENGINEERS (ASME) ................................ ................................................. 14 4.3.2. AMERICAN SOCIETY OF TESTING MATERIALS (ASTM) ................................... .................................................... 14 4.3.3. AMERICAN PETROLEUM INSTITUTE (API) ............................................. ........................................................... 14 4.3.4. BRITISH STANDARDS............................................................... ..................................................................... 15 4.3.5. ISA- INTERNATIONAL SOCIETY OF AUTOMATION (ISA) .......................................................................... 15 4.3.6. INTERNATIONAL ORGANIZATION FOR STANDARDIZATION (ISO) ............................................................................ 16 4.3.7. NATIONAL ASSOCIATION OF CORROSION ENGINEERS (**NACE**) .............................................................. 17 4.3.8. IEC STANDARDS .................................................................. ....................................................................... 17 4.4. ORDER OF PRECEDENCE............................................................. ............................................................ 17 5. AMMENDMENT TO ADNCO ONSHORE ENGINEERING STANDARD – SPECIFICATION OF SHUTDOWN VALVES FOR HIPPS AND SAFETY FUNCTION (DOC.NO.ES 30-99-39-0021).......................................................... 18 6. LANGUAGE AND ENGINEERING UNITS ................................................. ............................................... 27 6.1. GENERAL ........................................................................ .......................................................................... 27 6.2. ENGINEERING UNITS .............................................................. ..................................................................... 27 7. COMPLIANCE TO SPECIFICATIONS ................................................... .................................................... 28 7.1. ADHERENCE TO SPECIFICATIONS .................................................... ................................................................ 28 7.2. DESIGN LIFE .................................................................... .......................................................................... 28 8. ATTACHMENTS .................................................................... ................................................................ 28 8.1. ATTACHMENT-1: SPECIFICATION OF SHUTDOWN VALVES FOR HIPPS AND SAFETY FUNCTION (DOC.NO.30-99-39-0021) ......................................................... ............................................................................ 29
SIL | SPECIFICATION FOR ON OFF VALVES, SHUTDOWN VALVES AND BLOWDOWN VALVES Document No. : P16093-30-99-39-1604 Rev : 2 Project No. P16093 Agreement No. 4700021779 Page : 9 of 29 Security Code: 5 – Public ADNOC Classification: Public NDT : Non Desturctive Testing PDDL : Project Document Deliverable List PFD : Probability of Failure on Demand PQR : Procedure Qualifications Reports PST : Partial Stroke Test PVC : Poly Vinyl Chloride QMS : Quality Management System RDS : Remote Degassing Station SAT : Site Acceptance Test SDV : Shutdown Valve SFF : Safe Failure Fraction SIF : Safety Instrumented Function **SIL** : Safety Integrity Level SOV : Solenoid Valve SPIR : Spare Parts Interchangeability Record SSV : Surface Safety Valve TD : Technical Deviation TPI : Third Party Inspector VDRL : Vendor Document Deliverable List WAG : Water Alternating Gas
SIL | SPECIFICATION FOR ON OFF VALVES, SHUTDOWN VALVES AND BLOWDOWN VALVES Document No. : P16093-30-99-39-1604 Rev : 2 Project No. P16093 Agreement No. 4700021779 Page : 11 of 29 Security Code: 5 – Public ADNOC Classification: Public Document Number Document Title P16093-30-99-12-1602 Piping Material Specification 4.1.3 Design basis and Philosophies Document Number Document Title P16093-30-99-52-1601 Instrumentation & Control Design Basis P16093-30-99-91-1603 Process Design Basis P16093-30-99-23-1601 Piping Design Basis P16093-30-99-91-1617 Fire Protection and Fire & Gas Detection Philosophy P16093-30-99-89-1643 **SIL** Study Report P16093-30-99-52-1651 Control and Safety System Philosophy 4.2. COMPANY and SHELL Specifications & Standards 4.2.1. COMPANY Specifications Document Number Document Title ES 30-99-00-0001 Engineering Specification for Tag Plates for Field and Indoor Equipment ES 30-99-00-0102 Corrosion and Material Selection Philosophy ES 30-99-12-0030 Inspection and Test Plan for Piping Valves ES 30-99-12-3208 Specification for Pipeline Valves ES 30-99-12-3209 Specification for Piping Valves ES 30-99-00-8517-1 Equipment / Material Critically Rating
ISO 5208 | SPECIFICATION FOR ON OFF VALVES, SHUTDOWN VALVES AND BLOWDOWN VALVES Document No. : P16093-30-99-39-1604 Rev : 2 Project No. P16093 Agreement No. 4700021779 Page : 16 of 29 Security Code: 5 – Public ADNOC Classification: Public Document No. Document Title ISA-71.01 Environmental Conditions for Process Measurement and Control Systems: Temperature and Humidity ISA-71.02 Environmental Conditions for Process Measurement and Control Systems: Power ISA-71.03 Environmental Conditions for Process Measurement and Control Systems: Mechanical Influences ISA-71.04 Environmental Conditions for Process Measurement and Control Systems: Airborne Contaminants ISA-82.03 Safety Standard for Electrical and Electronic Test, Measuring, Controlling, and Related Equipment 4.3.6. International Organization for standardization (ISO) Document No. Description ** - ISO 5208** Industrial Valves - Pressure Testing of Metallic Valves - ISO 9001 Quality Management Systems – Requirements - ISO 10423 Petroleum & Natural Gas Industries-Drilling & Production Equipment- Wellhead & Christmas Tree - ISO 12490 Mechanical Integrity and Sizing of Actuators And Mounting Kits for Pipeline Valves - ISO 14313 Pipeline Transportation Systems —Pipeline Valves
NACE | SPECIFICATION FOR ON OFF VALVES, SHUTDOWN VALVES AND BLOWDOWN VALVES Document No. : P16093-30-99-39-1604 Rev : 2 Project No. P16093 Agreement No. 4700021779 Page : 17 of 29 Security Code: 5 – Public ADNOC Classification: Public 4.3.7. NATIONAL ASSOCIATION OF CORROSION ENGINEERS (**NACE**) Document No. Description **NACE** MR0175 / - ISO 15156 Petroleum And Natural Gas Industries — Materials for Use in H2S-Containing Environments in Oil and Gas Production 4.3.8. IEC Standards Document No. Description - IEC 60079 Explosive Atmospheres - IEC 60189 Low-Frequency Cables and Wires with PVC Insulation and PVC Sheath - IEC 60331 Tests for Electric Cables Under Fire Conditions - IEC 60332 Tests On Electric and Optical Fiber Cables Under Fire Conditions - IEC 60529 Degrees Of Protection Provided by Enclosures (IP Code) IEC61000 Electromagnetic Compatibility (EMC) - IEC 61508 Functional Safety of Electrical / Electronic / Programmable Electronic Safety-Related Systems - IEC 61511 Functional Safety - Safety Instrumented Systems for The Process Industry Sector - IEC 62381 Automation Systems in The Process Industry - Factory Acceptance Test (FAT), Site Acceptance Test (SAT), And Site Integration Test (SIT) 4.4. ORDER OF PRECEDENCE All design and construction shall be performed in accordance with the Specifications, Standards, Codes, Regulations, latest Shell DEPs, etc. listed in the Contract. In any areas of conflict, the order of precedence of different applicable standards, specifications and project specifications shall follow the order: ➢ The laws, standards, and Regulations of United Arab Emirates ➢ ADNOC HSE Standards, HSE manuals and policies.
SIL | SPECIFICATION FOR ON OFF VALVES, SHUTDOWN VALVES AND BLOWDOWN VALVES Document No. : P16093-30-99-39-1604 Rev : 2 Project No. P16093 Agreement No. 4700021779 Page : 26 of 29 Security Code: 5 – Public ADNOC Classification: Public Section Amendment The MRB shall contain at least and not limited to the following items; - Material Requisition including data sheets - Purchase Order "PO" (un-priced) - As built drawings and shall be provided with review, appraisal, validate and approval provisions - Engineering and design calculations provided with review, appraisal, validate and approval provisions. - Inspection and Test Plans - Welding logs and Weld Maps - Welding Procedure Specifications (WPS's) and Procedure Qualifications Reports (PQR's) - Non- Destructive Test Procedures - NDT scope of work and NDT log/register - Hydro test / pressure Test Procedure - Heat treatment procedure - Heat Treatment Plan - Painting / coating records and test certificates - Material Test Certificates summary and traceability log/register supported with Material Test Certificates - Testing Procedures - Functional test and **SIL** certificates - Sub-Orders Index and Orders - Inspection Release Notes - Master log/register of NCR's and Analysis of NCR’s - Technical Deviation(s) - Packing & handling procedure - Final product certificates such as "Certificate of Conformity" - Close out report including all Quality concerns and all lessons Learned covering both positive and negative aspects. All prior approved documents must show the signed acceptance stamp of the PURCHASER. The Manufacturing Record Book shall be complete for final inspection and submitted to the Inspector prior to material dispatch. Following Inspectors acceptance,